## Front & Preliminaries
|  |  |  | SPECIFICATION | June
|  |  |  | S-704L | 2020
Information Requirements for
High Voltage Three Phase Cage
Induction Motors
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | June 2020 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
S-704L Information Requirements for
High Voltage Three Phase Cage Induction Motors
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
S-704L Information Requirements for
High Voltage Three Phase Cage Induction Motors
Introduction
The purpose of this information requirements specification (IRS) is to define Information requirements for the supply of high voltage three phase cage induction motors in accordance with IOGP S-704 for application in the petroleum and natural gas industries. This document defines the information requirements, including format, timing and purpose, for information to be provided by the manufacturer. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the supplementary requirements specification IOGP S-704, quality requirements specification IOGP S-704Q and equipment data sheet IOGP S-704D which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Supplier Instructions
S-704L Information Requirements for
High Voltage Three Phase Cage Induction Motors
Supplier Instructions
In response to Invitation To Tender (ITT)
Tenderers to submit information as defined in column E - 'Submit At Proposal' in 'Requirements' sheet, in accordance with ITT instructions
On award of contract
Specified Information requirements shall be submitted in accordance with contract information submission instructions. Suppliers to prepare and submit 'Supplier Master Information Schedule' (SMIS) incorporating information requirements in accordance with columns F - 'First Issue Post Purchase Order' in 'Requirements' sheet. Supplier to demonstrate compliance with each information requirement either by providing document number cross reference to the Requirement in 'Supplier Master Information Schedule' (SMIS) and, if specified in the Contract, using column J 'Fulfilled by Document Number(s)' in the IRS Requirements Sheet.
On completion of scope
Supplier to validate that the information delivered meets the IRS requirements either through cross reference to the deliverable type in a as-built version of the 'Supplier Master Information Schedule' SMIS and, if specified in the Contract, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in Requirement sheet populated with the specific document numbers issued to the Purchaser.
IRS Structure Contents
1 |  | 'Front & Preliminaries' Tab
The 'Front & Preliminaries ' tab includes an IOGP Front sheet for the IRS followed by Acknowledgements, a Disclaimer, Copyright Notice, Foreword and Introduction
2 |  | 'Supplier Instructions' Tab
This 'Supplier Instructions' tab provides instructions that Suppliers are to follow in response to this IRS.
3 |  | 'Requirements' Tab
The 'Requirements' tab lists the suite of information requirements that are to be supplied during tendering and following award of the purchase order to deliver the purchase order scope. The information requirements are grouped under three broad categories; Management information requirements: Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. Technical information requirements: Technical information developed by the supplier or their sub suppliers, during the design and development, acquisition, manufacture, assembly and testing of the contracted scope. Purchase Order Specific Information Requirements: Information requirements specified by individual owners-operators in addition to those specified by IOGP-JIP33 to meet specific operational, project or legislative requirements. Note: Information requirements relating to contractual and administrative terms and conditions or regulatory obligations are to be supplied in accordance with the applicable purchase order or regulation. "The 'Requirements' tab includes columns A to L, including Column A for the relevant requirement code and Column B for the Requirement for the different Information Requirements (Data, Documents and/or Models) to be provided by suppliers, based on the parent standard, IOGP Specification or the specified parent industry Standard. Condition Invoking Revoking Requirement Column C is included to allow any specific conditions to be identified that may require a additional deliverable(s). Typical Deliverable Column D is provided for Purchaser to identify the deliverable type that the information would typically appear within; this also allows the Purchaser's Requisitioning Engineers to group the various Information Requirements by Deliverable Type. Column E includes Submission Requirements (Yes or No) at Proposal, while columns F, G & H identify Issue Purpose (For Information or For Acceptance) and Durations (Period or Weeks/Months) for First Issue of the particular deliverable Post Purchase Order. Required As Built, Fulfilled by Document Number(s), Translation Required and Remarks columns I, J, K & L are also included. Definitions for each column are contained in the rows above the columns: Abbreviations used for various submission requirements in Column H are shown in table 3.1 below:
Table 3.1 - Information Submission Abbreviations
4 |  | 'Definitions' Tab
The 'Definitions' tab includes several columns A to F, including Column A for the relevant Code & Column B for the Requirement for the different Information (Data, Documents and/or Models) Requirements to be provided by Suppliers, all copied from the 'Requirements' tab. Column C includes a full description of the Information Requirement based on the Parent Standard, IOGP Specification or an Industry Standard. Column D gives a reference to the Parent Standard, IOGP Specification or an Industry Standard that the Information requirement is identified in. Column E identifies the Requirement format as listed in Table 9.1 below. Column F relates the CFIHOS discipline document type that could be used to classify the document having this IRS content. Definitions for each column are contained in the rows above the columns:
5 |  | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various tabs of this workbook.
Buyer |  |  | Organisation placing a Contract or Purchase Order with Supplier for equipment or services on project; may be alternatively referred to as 'User' or 'Purchaser'
CFIHOS |  |  | Capital Facilities Information Hand Over Specification
Company |  |  | Project Operating Entity or the organisation Contractor is under contract to
Contractor |  |  | Project Contractor responsible for procuring equipment.
Information |  |  | Data, Documents and/or Models
IRS |  |  | Information Requirements Specification
PO |  |  | Purchase Order
QRS |  |  | Quality Requirements Specification
SMIS |  |  | Supplier Master Information Schedule
Supplier |  |  | Organisation supplying equipment or services to Company and/or Contractor on project; may alternatively be referred to as "Vendor", "Seller" or “Manufacturer”.
6 |  | CFIHOS
The Information Requirements are also classified according to document classification published in v1.4 of Capital Facilities Information Hand Over Specification (CFIHOS). The objective of CFIHOS is to create a common information standards across the process industries. Further information on CFIHOS can be found at:
https://uspi.nl/index.php/projects/frameworks-methodologies/136-cfihos
7 |  | Document Metadata
Typical Metadata for Information Deliverables to be provided by Suppliers is shown in Table 7.1 below
Table 7.1 - Supplier Deliverable Metadata
8 |  | Deliverable Formats
The format of the relevant Information Deliverable to be submitted by Supplier for Buyer/Contractor is to be as described in table 8.1 below. Where required to be ‘As Built’, deliverables are to be updated and handed over in the native format.
Table 8.1 – Deliverable Formats
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
S-704L Information Requirements for High Voltage Three Phase Cage Induction Motors
Requirements
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement based on the description in the Parent Standard, IOGP Specification or an Industry Standard Information Requirement Title.
C | Condition Invoking Requirement - describes special condition(s) under which the Information Requirement is required; e.g.. service offshore and weight greater than 1 tonne means information is required. NB: if blank, always required
D | Typical Deliverable - Purchaser to advise the short description of the Information Deliverable that would typically include this Information Requirement
E | Submit With Proposal - Yes or No, where 'Yes' means the Information Requirement is required to be submitted with Suppliers Proposal or 'No' is not required
F, G & H | First Issue Post Purchase Order - issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the Information Requirement and Period defined after Purchase Order placement.
I | Required As Built - Yes or No, where 'Yes' means the Information Requirement is required to be 'As Built' on completion or delivery of equipment or 'No' is not required 'As Built'
J | Fulfilled by Information Deliverable Number(s) - identifies which Information Requirement(s) listed in the Supplier Master Information Schedule (SMIS) addresses the Purchasers requirements. NB; it should be noted that one Information Deliverable can fulfil more than one Information Requirement.
K | Translation Required -Yes or No, where 'Yes' means the Information Requirement should be translated into a language(s) (to be advised) other than English and 'No' means to be provided in English
L | Remarks - may include bid clarification questions & decisions (specify author & date)
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S704-IR-20 | Supplier master information schedule |  | Information Deliverables List | No | For Acceptance |  | WAO | Yes |  | No
S704-IR-21 | Quality plan | - | Quality Plan | No | - |  | - | - |  | -
S704-IR-22 | Inspection and test plan | - | Inspection and Test Plan (ITP) | No | - |  | - | - |  | -
S704-IR-23 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S704-IR-24 | Non-conformance records |  | Nonconformance History | No | For Acceptance |  | WAO | No |  | -
S704-IR-25 | Concession requests |  | Concession request | No | For Acceptance |  | WAO | Yes |  | No
Technical Information Deliverables
S704-IR-26 | General arrangement drawing | - | General arrangement diagram | Yes | For Acceptance |  | WAO | No |  | No | Preliminary with proposal
S704-IR-49 | Detail drawing(s) | - | Detailed drawing | Yes | For Information |  | WAO | No |  | No | Preliminary with proposal
S704-IR-45 | Foundation loading details | - | Foundation loading diagram | Yes | For Acceptance |  | WAO | No |  | No | Preliminary with proposal
S704-IR-27 | Termination diagram | - | Termination diagram | No | For Acceptance |  | WAO | No
S704-IR-28 | Single-speed motor performance curves | - | Motor performance & electrical data and curves | - | For Acceptance |  | WAO | No
S704-IR-29 | Converter-fed motor performance curves | Where purchaser confirms the motor is converter-fed. | Motor performance & electrical data and curves | Yes | For Acceptance
S704-IR-42 | Thermal limit curves | Selected in data sheet | Motor performance & electrical data and curves | No | For Acceptance |  | WAO | No |  | No
S704-IR-30 | Routine test procedure | - | Routine test procedure | No | For Acceptance |  | WPTT | No
S704-IR-31 | Routine test report | - | Routine test report | No | For Acceptance |  | - | - |  | -
S704-IR-33 | Noise type test report | Where a type test has been performed on an identical motor or where a special test has been specified as per S-704 Table 16C | Type test report | No | For Information |  | WPTD | No
S704-IR-44 | Lateral vibration analysis report | When specified in the data sheet | Lateral vibration analysis report | No | For Acceptance |  | - | - |  | -
S704-IR-43 | Torsional analysis report | Converter-fed motors with a power rating equal or greater than 5 MW or motors with a variable torque load or when specified in the data sheet | Torsional analysis report | No | For Acceptance |  | - | - |  | -
S704-IR-35 | Data for protection setting/power modelling | Data for protection setting/power modelling requested in the datasheet | Data for protection setting/power modelling | No | For Acceptance |  | WAO | No
S704-IR-36 | Equivalent circuit diagram | - | Equivalent circuit diagram | No | For Acceptance |  | WAO | No
S704-IR-37 | Installation, operation and maintenance manual |  | Installation, operation and maintenance manual | No | For Information |  | WAO | No |  | No
S704-IR-48 | Lubrication data sheet | - | Lubrication list | No | For Information |  | WAO | No |  | No
S704-IR-46 | Special tools | - | Special Tools List | No | For Information |  | WAO | No |  | No
S704-IR-38 | Ex certification |  | Ex certification | No | For Information |  | WAO | No |  | No
S704-IR-50 | General certification |  | Lifting appliance certificate | No | For Information |  | WAO | No |  | No
S704-IR-39 | Declaration of conformity |  | Declaration of conformity | No | For Information |  | WPTD | No |  | No
S704-IR-40 | S-704D Data Sheet |  | Data Sheet | Yes | For Acceptance |  | WAO | Yes |  | No | Preliminary information should be provided with proposal.
S704-IR-47 | Spare parts list | - | Spare Part List | No | For Information |  | WAO | No |  | No
Purchase Order Specific Information Requirements
S704-IR-41 | Insert Purchase Order Specific Requirements |  | Insert Purchase Order Specific Requirements | - | - |  | - | - |  | -
Public Review Draft
Public Review Draft

## Definitions
S-704L Information Requirements for High Voltage Three Phase Cage Induction Motors
Definitions
Column | Heading - Details and requirements
A | Code - a unique identifier for the Information Requirement assigned by IOGP JIP33 DigitalTool
B | Requirement - a short description of the Information Requirement that would typically provide the Information required, based on the description in the Parent Standard, IOGP Specification or an Industry Standard Title.
C | Description - an excerpt from the Parent Standard, IOGP Specification or Industry Standard.
D | Reference - reference to the Parent Standard, IOGP Specification or Industry Standard that the Information Deliverable is identified in.
E | Format - defines the required format of the relevant Information Requirement to be submitted by Supplier for Purchaser/Contractor for information and acceptance as shown in Table 9.1 of Instructions Tab and selected from pick list.
F | CFIHOS Discipline Document Type Code - the CFIHOS discipline document type that could be used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Discipline Document Type Code
Contract Management Information Deliverables
S704-IR-20 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | API 671, 13.1.1 | Native | CFIHOS-70000099
S704-IR-21 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] | Contract Requirement | PDF
S704-IR-22 | Inspection and test plan | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | Contract Requirement | PDF | CFIHOS-70000180
S704-IR-23 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials including lubricants required etc., both prior to installation and post installation, but prior to commissioning. e. special mechanical handling precautions | Contract Requirement : 6.6 | PDF | CFIHOS-70000154
S704-IR-24 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. | Contract Requirement | PDF | CFIHOS-70000226
S704-IR-25 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout | Contract Requirement | PDF | CFIHOS-70000389
Technical Information Deliverables
S704-IR-26 | General arrangement drawing | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards. For equipment / components the drawing may include cross sectional views. Document to contain the following information: • Main dimensions • Heat exchanger dimensions and location • Dimensions and location of all terminal boxes • Interface connections (inc.piping connections where applicable) • Weight • Centre of gravity • Installation and mounting details • Lifting arrangement • Location of jacking points • Location of drain holes • Earthing and bonding points • Greasing points (where applicable) |  | PDF | CFIHOS-70000153
S704-IR-49 | Detail drawing(s) | Detail drawing to provide details of external and internal components of the motor. Method of assembly showing how sub-components are constructed including fixings and gaskets. All components to be labelled using terminology consistent to that found in other manufacturer drawings and documentation. Detail drawings will be large and include details not found on general arrangement drawing. |  | PDF | CFIHOS-70000116
S704-IR-45 | Foundation loading details | Document or drawing detailing foundation loads to permit adequate foundation design by the purchaser. This shall include the following items: • the size and location of foundation bolts; • the weight distribution for each bolt and sub-soleplate location; • any unbalanced forces or moments generated by the motor in the specified operating range; • the location of the center of gravity; and • foundation forces as a result of worst case transient conditions. |  | PDF | CFIHOS-70000151
S704-IR-27 | Termination diagram | A diagram which identifies all connections and cable terminations to facilitate installation, removal, maintenance and fault finding of package equipment. To include vendor interfaces. • Termination diagram will include as a minimum where applicable: • Space heater terminations • Cooling and heat exchanger component terminations • Vibration monitoring device terminations • Temperature sensor terminations • Differential protection current transformers terminations • Partial discharge sensor terminations |  | PDF | CFIHOS-70000330
S704-IR-28 | Single-speed motor performance curves | Motor performance curve shall include the following information: • Torque curve from 0 to 100% synchronous speed at 80% rated voltage expressed as a percentage of rated torque. • Torque curve from 0 to 100% synchronous speed at 100% rated voltage expressed as a percentage of rated torque. • Current curve from 0 to 100% synchronous speed at 80% rated voltage expressed as a percentage of rated current. • Current curve from 0 to 100% synchronous speed at 100% rated voltage expressed as a percentage of rated current. • Torque curve of the load from 0 to 100% synchronous speed expressed as a percentage of rated torque. • Power factor curve from 0 to 100% synchronous speed rated at 100% rated voltage |  | PDF
S704-IR-29 | Converter-fed motor performance curves | Provide motor performance curves for quadrant operation specified in the datasheet and as per IEC 61800-4: 2002 section 6.1.3 |  | PDF
S704-IR-42 | Thermal limit curves | The motor vendor shall provide motor thermal capacity data necessary for the purchaser to determine the waiting time before allowing a restart and to develop settings for the thermal time constant in the motor protective relay. As a minimum, this data shall include the following: a) thermal limit curves (per IEEE 620) with the motor initially at ambient temperature; b) thermal limit curves (per IEEE 620) with the motor initially at rated temperature; c) acceleration time curves with the defined shaft load at rated voltage and at the starting voltage conditions specified in API 541 Section 4.2.3 (2014); d) required wait time prior to another start after exhausting the defined number of starts, with the motor running at rated load; and e) required wait time prior to another start after exhausting the defined number of starts, with the motor stopped.
S704-IR-30 | Routine test procedure | Procedure to detail all tests specified in S-704 Table 16A or Table 16B on the fully assembled motor. Procedure to define test set-up and test equipment. Test procedure to include type tests where they have not been performed previously as defined in S-704 Tables 16A Note a) and Table 16B Note a) Test procedure to include special tests as defined in S-704 Table 16C where they are specified in the data sheet. | 9.1.1.1, Table 16A, Table 16B, Table 16C | PDF
S704-IR-31 | Routine test report | This document records and documents all results from the activities performed in routine tests, type tests and special tests in accordance with S-704 Section 9. • Mandatory content of information: • Date of testing; • Signature of person responsible for test; • Object identification (type, series number, etc.). • Measured values; • Statement of compliance; • Test equipment / instruments used; • Reference to test procedure. | 9.1.1.1, Table 16A, Table 16B, Table 16C | PDF
S704-IR-33 | Noise type test report | A noise test report detailing noise performance in accordance with IEC 60034-9. |  | PDF
S704-IR-44 | Lateral vibration analysis report | When specified, the vendor shall provide a lateral vibration analysis of the machine to assure acceptable amplitudes of vibration at any speed from zero to maximum operating speed. Test report to include, but is not limited to the following: • Foundation stiffness and damping • Support, stiffness mass and damping characteristics • Bearing lubricant film stiffness and damping characteristics • Starting conditions, operating speed ranges, trip speed and coast-down conditions • Rotor masses • Mass moment of the coupling half • Asymmetrical loading • Rolling element bearing stiffness and damping values (where applicable) • Location and orientation of radial vibration probes • Unbalanced magnetic pull The lateral vibration analysis report shall include all the model details to allow for an independent audit of lateral and stability analysis. | 11.12 | PDF
S704-IR-43 | Torsional analysis report | The torsional analysis report is to include, but is not limited to the following: • a complete description of the method used to complete the analysis; • a graphic display of the mass-elastic system; • a tabulation identifying the polar mass moment of inertia and torsional stiffness for each component identified in the mass-elastic system; • a graphic display or expression of any torsional excitation versus speed or time; and • a graphic display of torsional critical speeds and deflections (a mode shape diagram) |  | PDF
S704-IR-35 | Data for protection setting/power modelling | Additional information to facilitate power system modelling and/or protection device configuration. Final application specific information requirements to be agreed between purchaser and supplier. |  | PDF
S704-IR-36 | Equivalent circuit diagram | A function diagram providing information on the electric and magnetic behaviour of the motor. This shall apply the conventions for electric and magnetic circuits as specified in IEC 60375. See IEC TS 60034-25 Table 3 for electrical parameters to be included in the T-equivalent circuit diagram. |  | PDF
S704-IR-37 | Installation, operation and maintenance manual | The user of the product shall be provided with information regarding normal and safe operation/functioning. As appropriate, this should be completed by information regarding automatic and remote controlled products, exceptional functions/situations, indications to be observed, protection of persons and instructions for fault detection. Description of methods of installing a piece of equipment. The instruction material shall contain applicable information relating to the product itself as follows : Installation: • Installation refers to the mounting, setting, erection, etc. Operation: • detailed description of the product, its fittings, its guards and/or protective devices; • comprehensive range of applications for which the product is intended, taking into account variations of the original machine if appropriate; • warnings about reasonably foreseeable misuse; • instructions for setting and adjustment; • instructions for re-starting after an intervention; • diagrams showing the main functions of the product and especially the safety functions; • description of the initial operations required to bring the product to full working performance, with details of checks, methods of setting adjustable controls and what the setting should be; • maintenance tasks within the capability of the user during normal use; • identification and treatment of malfunctions; • details of any techniques that are likely to be new to users, for example with regard to information technologies; • storage and preservation of the product when not in use. Maintenance: The document shall include descriptions for both hardware and software regarding preventive maintenance, fault detection, fault diagnosis and fault isolation, rectification of faults and system operation. The instructions should include information concerning: • the nature and frequency of inspections; • safety precautions and warnings for maintenance carried out on running or live equipment; • information for fault diagnosis and identification; • instructions for repairs and adjustments; • description of built-in diagnostic systems to aid fault finding, when applicable; • drawings and diagrams enabling maintenance personnel to carry out their task rationally (especially fault-finding tasks); • regular checking of warning devices; • description of all predictable tasks performed at specific intervals to be consolidated in the form of maintenance schedules and, if necessary, master schedules; • the name, address, telephone number, etc. of the supplier or others from whom technical assistance can be obtained. |  | PDF | CFIHOS-70000181, CFIHOS-70000206, CFIHOS-70000228
S704-IR-48 | Lubrication data sheet | Data sheet confirming all lubrication details required for motor maintenance and operation. To include but not limited to the following information: Bearing type(s) For rolling element bearings: Re-greasing amounts per bearing Re-greasing intervals according to running speeds and ambient temperatures Re-greasing procedure Grease type (recommended product reference code and specification) For sleeve bearings: Oil change intervals Top-up procedure Lube oil type (recommended product reference code and specification) |  | PDF | CFIHOS-70000228
S704-IR-46 | Special tools | Document detailing where special tools (tools specific for motor assembly and disassembly) are required and instructions for their use. |  | PDF
S704-IR-38 | Ex certification | Certificates issued by a recognised notified or certification body e.g. ATEX Directive, IECEx, EAC, certifying the motor and all auxiliary components have satisfied specified criteria to enable their use in a potentially explosive atmosphere. | 15.1.2 | PDF | CFIHOS-70000160
S704-IR-50 | General certification | Certificates confirming the motor and all auxiliary components have satisfied specified criteria to enable their use. Typically this will included the following where required: • Lifting appliance certification • Certification of welded joints • Certification of pressurized system • Material certification • Calibration certification |  | PDF | CFIHOS-70000160
S704-IR-39 | Declaration of conformity | Declares conformance with all standards relating to the motor in it's region of use as defined by the purchaser in the specification. |  | PDF
S704-IR-40 | S-704D Data Sheet | S-704D with all supplier fields populated. | 11.3.7.1.1, 11.3.7.1.2, 11.3.7.3.9, 11.3.7.4.1, 11.3.7.4.10, 11.5.4.7, 11.5.4.8, 11.7.3, 11.7.4, 15.5.1, 6.8.1, 9.1.2.2, 9.14.1, 9.14.2, 9.15.1, 9.16.1, 9.16.2, Table 22 | Native | CFIHOS-70000416
S704-IR-47 | Spare parts list | A document detailing commissioning spare parts list and 2 year operational spare parts list. This list shall also include the following as a minimum: • Part name • Quantity • Service interval • Service action description (e.g. for replacement of d-end bearing) • Supplier part number (where applicable) • Original manufacturer • Original manufacturer part number |  | PDF | CFIHOS-70000374
Purchase Order Specific Information Requirements
S704-IR-41 | Insert Purchase Order Specific Requirements | Insert Purchase Order Specific Requirements |  | PDF
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Backcover
Month XXXX
Public Review Draft

## Pick Lists
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col K
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)ï¿½ | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
WAO
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: