## Front & Preliminaries
|  |  |  | SPECIFICATION | September 2022
|  |  |  | IOGP S-714-1L | Version 0.1
Information Requirements for
Diesel Generator Package
(ISO/IEC Offshore)
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | September 2022 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-714-1L (0.1) Information Requirements for
Diesel Generator Package (ISO/IEC Offshore)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-714-1L (0.1) Information Requirements for
Diesel Generator Package (ISO/IEC Offshore)
Introduction
The purpose of this information requirements specification (IRS) is to define information requirements for the procurement of diesel generator package (ISO/IEC Offshore) in accordance with IOGP S-714-1 for application in the petroleum and natural gas industries. The IRS defines the information requirements, including format, timing and purpose, for information to be provided by the supplier. It also defines the specific conditions which must be met for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
This IRS shall be used in conjunction with the specification (IOGP S-714-1), procurement data sheet (IOGP S-714-1D) and quality requirements specification (IOGP S-714-1Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Information Requirements Specification
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Instructions
IOGP S-714-1L (0.1) Information Requirements for
<Diesel Generator Package (ISO/IEC Offshore) Title>
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS Structure Contents
| 1 | 'Front & Preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes / No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information Submission Abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS .
Column K — 'Translation Required' (Yes / No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable Formats
Column F — 'CFIHOS Discipline Document Type Code' relates to the CFIHOS discipline document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3 below. Metadata listed below are as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The document master to which this revision is related |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification |  |  | The Export Control Rule that is applicable for the document revision (e.g., ECCN, EAR). |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
| Security classification |  |  | Indicates internal Owner-Operator access restriction applicable for the document |  |  | TBA
Table 3 — Supplier Deliverable Metadata
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
IOGP S-714-1L (0.1) Information Requirements for Diesel Generator Package (ISO/IEC Offshore)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Information Deliverable Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S7141-IR-29 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | WAO | - |  | -
S7141-IR-21 | Delivery schedule |  | Delivery/Production schedule | Yes | For Information |  | WAO | - |  | -
S7141-IR-22 | Progress report |  | Progress report | No | For Information |  | WAO (Monthly) | - |  | -
S7141-IR-23 | Quality plan |  | Quality plan | Yes | For Information |  | WAO | - |  | -
S7141-IR-24 | Sub-supplier list | Required for CAS A, CAS B, CAS C | Sub-supplier list | - | - |  | - | - |  | -
S7141-IR-25 | Inspection and test plan for complete package |  | Inspection and test plan (ITP) | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-26 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | - |  | -
S7141-IR-27 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | WAO | - |  | -
S7141-IR-28 | Concession requests |  | Concession request | No | For Acceptance |  | WAO | - |  | -
Technical Information Deliverables
Analysis
S7141-IR-54 | Torsional critical speed analysis |  | Torsional critical speed analysis | No | For Acceptance |  | WAO | - |  | -
Calculation and Curves
S7141-IR-57 | Battery sizing calculation |  | Design calculation | No | For Acceptance |  | WAO | - |  | -
S7141-IR-55 | Diesel engine sizing calculation and performance curves |  | Curves and tables calculations | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-60 | Generator performance curves |  | Curves and tables calculations | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-59 | Structural design calculation |  | Design calculation | No | For Acceptance |  | WAO | - |  | -
S7141-IR-58 | Ventilation calculation |  | Heat dissipation calculation and loads | No | For Information |  | WAO | - |  | -
Certificates
S7141-IR-72 | Certificate of conformance - third party |  | Certificate of conformance | No | For Information |  | WAO | - |  | -
Data
S7141-IR-35 | Diesel engine data sheet |  | Manufacturer datasheet | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-33 | Generator data sheet |  | Manufacturer datasheet | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-34 | Instrument data sheet |  | Manufacturer datasheet | No | For Acceptance |  | WAO | - |  | -
S7141-IR-32 | Noise data sheet |  | Noise data sheet | Yes | For Acceptance |  |  | - |  | -
Drawing
S7141-IR-46 | Cause and effect diagram |  | Cause and effect diagram | No | For Acceptance |  | WAO | - |  | -
S7141-IR-49 | Coupling drawing |  | Equipment cross section diagram | No | For Information |  | WAO | - |  | -
S7141-IR-50 | General arrangement drawing - diesel engine |  | General arrangement diagram | No | For Information |  | WAO | - |  | -
S7141-IR-42 | General arrangement drawing - diesel generator package |  | General arrangement diagram | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-41 | General arrangement drawing - generator |  | General arrangement diagram | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-47 | Layout diagram - lighting |  | Layout diagram | No | For Acceptance |  | WAO | - |  | -
S7141-IR-45 | Logic diagram |  | Logic diagram | No | For Acceptance |  | WAO | - |  | -
S7141-IR-38 | Piping and instrumentation diagram |  | Piping and instrumentation diagram | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-40 | Schematic drawing |  | Schematic diagram | No | For Information |  | WAO | - |  | -
S7141-IR-43 | System topology diagram |  | System topology diagram | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-44 | Termination diagram |  | Termination diagram | No | For Acceptance |  | WAO | - |  | -
S7141-IR-39 | Wiring diagram |  | Wiring diagram | No | For Acceptance |  | WAO | - |  | -
List
S7141-IR-67 | Bill of materials |  | Bill of materials | No | For Information |  | WAO | - |  | -
S7141-IR-68 | Utility consumption list |  | Consumption data and load list | Yes | For Acceptance |  | WAO | - |  | -
S7141-IR-74 | Input/output list |  | Input, output list | No | For Acceptance |  | WAO | - |  | -
S7141-IR-69 | Instrument list |  | Instrument list | No | For Acceptance |  | WAO | - |  | -
S7141-IR-76 | Spare part list |  | Spare part list | Yes | For Acceptance |  | WAO | - |  | -
Manual
S7141-IR-52 | Operating manual |  | Operating manual | No | For Acceptance |  | WAO | - |  | - | Operating manual index, if required, shall be provided in first revision of the document. When the index has been agreed, operating manual content shall be provided in subsequent revision of the document.
S7141-IR-51 | Maintenance manual |  | Maintenance manual | No | For Acceptance |  | WAO | - |  | - | Maintenance manual index, if required, shall be provided in first revision of the document. When the index has been agreed, maintenance manual content shall be provided in subsequent revision of the document. Recommended schedules for major and minor overhauls shall be provided at proposal stage to include list of required spare parts, estimate of required time and manpower.
Procedures
S7141-IR-64 | Diesel generator package performance test procedure |  | Factory acceptance test (FAT) procedure | No | For Acceptance |  | WAO | - |  | -
S7141-IR-65 | Surface protection procedure |  | Painting and coating procedure | Yes | For Acceptance |  | WAO | - |  | -
Records
S7141-IR-63 | Diesel generator package performance test records |  | Factory acceptance test (FAT) records | No | For Acceptance |  | WAT | - |  | -
S7141-IR-61 | Manufacturer record book (MRB) |  | Manufacturer record book | No | For Acceptance |  | WAD | - |  | - | Manufacturer record book index, if required, shall be provided in first revision of the document. When the index has been agreed, manufacturer record book content shall be provided in subsequent revision of the document.
S7141-IR-62 | Noise test records |  | Noise test records | No | For Acceptance |  | WAT | - |  | -
Reports
S7141-IR-71 | Material handling report |  | Lifting procedure | No | For Acceptance |  | WAO | - |  | -
S7141-IR-70 | Type test report |  | Type test report | No | For Information |  | WAO | - |  | -
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
IOGP S-714-1L (0.1) Information Requirements for Diesel Generator Package (ISO/IEC Offshore)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Discipline Document Type Code — CFIHOS discipline document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S7141-IR-29 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | PDF | CFIHOS-70000099
S7141-IR-21 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S7141-IR-22 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S7141-IR-23 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF
S7141-IR-24 | Sub-supplier list | Definition of processes, products or services that will be externally provided and the controls to be applied by the DG package supplier to ensure conformance with agreed requirements. The list includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS) . Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | PDF
S7141-IR-25 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. This should include the sub-supplier equipment ITP. |  | PDF | CFIHOS-70000180
S7141-IR-26 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. |  | PDF | CFIHOS-70000154
S7141-IR-27 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S7141-IR-28 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
Technical Information Deliverables
Analysis
S7141-IR-54 | Torsional critical speed analysis | Torsional critical speed analysis report, including but not limited to the following: a. Complete description of the method used. b. Graphic display of the mass elastic model. c. Tabulation identifying the mass moment and torsional stiffness of each component identified in the mass elastic system. d. Graphic display of exciting frequencies versus speed and natural torsional frequency (Campbell Diagram). e. Graphic display of torsional critical speeds and deflection angle for torsional vibration (mode-shape plot). f. Effects of alternative coupling on analysis. | 5.7.2 | PDF
Calculation and Curves
S7141-IR-57 | Battery sizing calculation | Basis for battery rated/ specified current based on base cranking current and applying correction factor for ambient temperature, cranking time, starter motor efficiency, cell voltage etc. |  | PDF | CFIHOS-70000086
S7141-IR-55 | Diesel engine sizing calculation and performance curves | Diesel engine site rating calculation will be according to Section 7 of ISO 15550. Mandatory content of information: – Calculation methods used; – Input data; – Results; – Analysis of the results. Calculation will also demonstrate that engine site rating provides 10% margin over the DG power specified. Diesel engine curves to indicate power developed at output shaft, fuel consumption, emissions over the operating range and ambient temperatures, with specified inlet and exhaust pressure loss and varying speeds. Guarantee points shall be identified. [Torque, Power & Specific Fuel Consumption vs Speed @ min, max, ISO ambient temperature, @site elevation, @reference fuel composition.] |  | PDF
S7141-IR-60 | Generator performance curves | Curves to indicate torque and current against speed for 80% and 100% voltage conditions and at rated frequency, superimposed on driven equipment torque curve to confirm that there is adequate net torque for acceleration. The following performance curves are required for both 80% and 100% voltage: | 6.1.2 | PDF
1. Generator efficiency vs load
2. Stator damage curves
3. Reactive capability curves
4. Short circuit decrement and withstand curves
5. Saturation curves
6. V-curves
7. Voltage dip curves
S7141-IR-59 | Structural design calculation | Structural design report detailing the following shall be provided if stated in the data sheet: - Input data - Assumptions made - Load cases and load combinations analysed - Accidental design calculations - Factor of safety achieved - Documentation of lifting equipment where applicable | 4.7.1 | PDF | CFIHOS-70000086
S7141-IR-58 | Ventilation calculation | This document contains the ventilation calculation by the supplier based on the heat load produced by the diesel engine, the generator and the ambient. |  | PDF
Certificates
S7141-IR-72 | Certificate of conformance - third party | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). Includes - EMC compliance according to IEC 61000-6-2 for immunity and IEC 61000-6-4 for emissions for the diesel generator package, - ingress protection certificates for instruments. CE Marking, UL/FM Type Tests, ATEX etc., - conformity with ISO 8528 standards. | 1.1, 7.4 | PDF | CFIHOS-70000013
Data
S7141-IR-35 | Diesel engine data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document shall provide information on technical data and characteristics about material, products or systems and their environment for proper implementation. The proposal submission of this data sheet should be based on IOGP S-714D. | 4.1, 5.1.1, 5.1.2, 5.1.3, 5.1.4, 5.10.1, 5.2, 5.4.1, 5.4.2, 5.5.1, 5.5.2, 5.5.6, 5.6.1, 5.8.2, 5.9.1, 5.9.2 | PDF | CFIHOS-70000416
S7141-IR-33 | Generator data sheet | Document providing information on technical data and characteristics about AC generator according to IEC or NEMA. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document will provide information on technical data and characteristics about performance of the generator and include the following | 6.1.1, 6.1.2, 6.3, 6.4, 6.5, 6.6 | PDF | CFIHOS-70000416
reactances and resistances for saturated and unsaturated conditions -
DIRECT AXIS TRANSIENT REACTANCE, Xd’(%), QUADRATURE AXIS TRANSIENT REACTANCE, Xq’ (%), DIRECT AXIS SUB TRANSIENT REACTANCE, Xd” (%), and QUADRATURE AXIS SUB-TRANSIENT REACTANCE, Xq” (%).
Synchronous Direct Axis Xd,
Synchronous quadrature axis Xq,
Negative Sequence reactance X2,
Zero Sequence reactance X0,
Leakage reactance XL,
Potier reactance Xp,
Field Reactance,
Armature Reactance, Xa,
Rotor Reactance Xr, X0/R0,
Armature Resistance, Ra, X2/R2, X''d/Ra, and
Negative sequence resistance R2.
The proposal submission of this data sheet should be based on IOGP S-714D.
S7141-IR-34 | Instrument data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment. Document provides information on technical data and characteristics about material, products or systems and their environment for proper implementation. | Table 2 | PDF | CFIHOS-70000416
S7141-IR-32 | Noise data sheet | The equipment noise data sheet shall contain all the information that the equipment supplier requires to understand, comply with and measure compliance with, and the noise limits for the equipment to be supplied. The equipment noise data sheet shall be returned with the tender, with its guarantee section completed by the supplier, giving the following information: a) unsilenced sound power and sound pressure levels in octave bands, and the A-weighted overall levels of the equipment; b) sound power and sound pressure levels in octave-bands, and the A-weighted overall levels of the equipment, together with details of any silencing measures that are necessary to meet the specified noise limits; c) the minimum attainable sound power and sound pressure levels in octave bands, and the A-weighted overall levels, if the specified limits cannot be met; d) details of any tonal, impulsive, intermittent or fluctuating noise levels. Additionally the following information shall be given, where applicable: e) completed data/requisition sheets of any silencers and/or acoustic enclosures, if the tender comprises such silencing equipment. (Source: ISO 15664) |  | PDF | CFIHOS-70000225
Drawing
S7141-IR-46 | Cause and effect diagram | Matrix cross-referencing logic control signals actuating a set of corrective actions. To define logic control and shutdown functions, alarms, trips to ensure sufficient process safety and shutdown. | 4.6.1 | PDF | CFIHOS-70000409
S7141-IR-49 | Coupling drawing | A detail and cross sectional drawing with parts list to facilitate dismantling, repair and assembly of parts and components shall be included. Relevant for assemblies and smaller components within assemblies. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. The manufacturer's standard detail cross sectional drawing shall be delivered. Typical information may be: • Items list with reference to supplier's part number. • Material definition with reference to relevant standards (Source: IEC 61355-1, D00003) | 5.10.4 | PDF | CFIHOS-70000116
S7141-IR-50 | General arrangement drawing - diesel engine | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components of diesel engine. The drawing shall contain reference to main specifications and standards For equipment / components the drawing may include cross sectional views. Document may contain the following information: • Main dimensions • Interface connections • Weight • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement | 4.9 | PDF | CFIHOS-70000153
S7141-IR-42 | General arrangement drawing - diesel generator package | A drawing showing outline dimensions with arrangement of components and accessories of the diesel generator package, part references, including the following details - | 4.2, 4.3, 4.6.2, 4.7.1, 4.7.3, 4.8, 4.9, 5.10.1, 5.10.2, 5.3.1, 5.4.4 | PDF | CFIHOS-70000153
Size, type, rating and identification of all interfaces
Weight of the assemblies with overall erection weight
Main dimensions and interface locations
Shaft centerline height (if applicable)
Location of centre of gravity and lifting points
Foundation loads, installation and mounting details
Lifting arrangement
Maintenance weight of major components
Material handling provisions with withdrawal/installation and maintenance spaces
Details of acoustic enclosure, when applicable, including lighting, F&G detectors, extinguishant piping, noise attenuators at ventilation inlet and outlet, wall panel fire rating, wall panel blast design, etc.
S7141-IR-41 | General arrangement drawing - generator | The generator drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing will contain reference to main specifications and standards. For equipment / components the drawing may include cross sectional views, terminal boxes, etc. Document may contain the following information: • Main dimensions • Interface connections • Weight • Centre of gravity • Withdrawal/installation and maintenance space. • Installation and mounting details • Lifting arrangement • Terminal boxes • Generator technical data | 4.4, 4.9, 6.2, 6.6 | PDF | CFIHOS-70000153
S7141-IR-47 | Layout diagram - lighting | A diagram showing the location of lamps inside the enclosure relative to surrounding structures and equipment to achieve specified illumination level in the work area. |  | PDF | CFIHOS-70000277
S7141-IR-45 | Logic diagram | A graphical representation of a system using formal logic. It displays the existence of functional elements and the paths by which they interact with each other using SAMA symbols. | 4.6.1 | PDF | CFIHOS-70000248
S7141-IR-38 | Piping and instrumentation diagram | Description: The piping and instrument diagram (P&ID), based on the process flow diagram, represents the technical realization of a process by means of graphical symbols for equipment and piping together with graphical symbols or process measurement and control functions. Mandatory content of information: – Function or type of equipment, including drives, conveyors, as well as installed spares; – Identification number of equipment including drives, conveyors as well as installed spares; – Characteristic data of equipment; – Indication of line number, nominal diameter, pressure rating, material class and fluid class of all piping; - Identification of any special piping items; – Details of equipment, piping, valves and fittings, thermal insulation; – Process measurement and control functions with identification number; – Characteristic data of drives. Optional content of information: – Denomination of flow rates and amounts of energy or energy carriers; – Route and direction of flow of energy or energy carriers; – Type of essential primary elements and sensors; – Essential construction materials for equipment; – Elevation of platforms and approximate relative vertical position of equipment; – Reference designation for valves and fittings; – Denomination of equipment; - External piping interfaces. (Source: IEC 61355, D00043) | 4.2, 4.3, 4.7.3, 4.8, 5.1.5, 5.1.6, 5.10.3, 5.2, 5.4.2, 5.4.3, 5.4.4, 5.5.3, 5.5.4, 5.5.5, 5.6.2 | PDF | CFIHOS-70000292
S7141-IR-40 | Schematic drawing | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays etc.) and their relationships for control panels, lighting, heat tracing, earthing, etc. | 5.3.2, 5.3.3, 6.1.1, 6.5, 7.1, 7.2, 7.5.1, 7.7, 7.8, Table 2 | PDF | CFIHOS-70000328
S7141-IR-43 | System topology diagram | Systems Topology Block Diagram shall show overall configuration of systems and subsystems to give a functional understanding on a high level. Typical contents shall be: • All related systems and subsystems represented by blocks • Location of the equipment, either by text labelling of each block or by blocks located in dotted area boxes. • Interface between blocks shall be indicated |  | PDF
S7141-IR-44 | Termination diagram | A diagram for motors, panels, junction boxes, etc. identifies all connections and cable terminations at input/output rails. Required for removal/hook up purposes and modifications. To include purchaser interfaces. | 4.2, 4.3, 4.6.2, 7.6 | PDF | CFIHOS-70000330
S7141-IR-39 | Wiring diagram | Description: Diagram providing information on the circuitry of an object. Mandatory content of information: – Graphical symbols representing the objects; – Graphical symbols representing the connections among objects; – Reference designations; – Terminal designations; – Signal level conventions (applicable to logic signals). – Information necessary to trace paths and circuits (signal designations, location references) – Supplementary information necessary for the understanding of functions Optional content of information: – Technical data; – Reference to other documents; – Information about wiring performance; – Cable and cable core identification. (Source: IEC 61355, D00053) | 7.2, 7.3, Table 1 | PDF | CFIHOS-70000268
List
S7141-IR-67 | Bill of materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications. Note when agreed includes details of sub-suppliers and associated purchase orders. | Table 1 , Table 2 | PDF | CFIHOS-70000028
S7141-IR-68 | Utility consumption list | Document providing input to engineering for design of the customer's installation or utility arrangement. Document stating the normal and maximum consumption of e.g. electric power, diesel oil, compressed air, heating/cooling media etc., for the equipment(-s) or unit(-s). The following generalized index will be used: • Equipment tag no. • Type of consumption • Normal Mode - The mode of platform operation when main process, utility systems and other facilities are in operation. This mode of operation gives the peak power requirement. • Critical Mode - The mode of platform operation just after a generator shut down and only one generator is running. • Stabilized Mode - The same mode of platform operation as critical mode, but the situation is stabilized. • Emergency Mode - The mode of platform operation when main process, utility systems, supplies to existing facilities are shut down. - The main generators are shut down. - The emergency generator is running. The load list shall show individual consumers at various voltage levels and pressures. |  | PDF | CFIHOS-70000203
S7141-IR-74 | Input/output list | An authoritative collection of values with a relationship to a specific equipment. List to show input and output of an equipment (e.g. instrument, telecom equipment) connected to other equipments (e.g. distributed control system, programmable logic controller).The columns of this collection is specified and controlled. | Table 1 , Table 2 | PDF | CFIHOS-70000179
S7141-IR-69 | Instrument list | An authoritative collection of values with a relationship to instrumentation. The columns of this collection is specified and controlled. Also known as Instrument Index. It will include alarm and trip setting of the relevant instruments. |  | PDF | CFIHOS-70000418
S7141-IR-76 | Spare part list | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: – Item reference number; – Quantity; – Part number or global identifier (together with manufacturer / supplier); – Part name. Optional content of information: – Type designation; – Specifying technical data; – Descriptive technical data; – Mass, dimensions; – Mass, dimensions; – Typical sketch; – Reference to document; – Remark. (Source: IEC 61355, D00106) |  | PDF | CFIHOS-70000374
Manual
S7141-IR-52 | Operating manual | Description of methods of operating a piece of equipment or process unit, including but not limited to instructions, procedures, drawings, tables, etc. for the operation -stop, start, and emergency shutdown. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 7.7, 7.8, Table 1 , Table 2 | PDF | CFIHOS-70000228
S7141-IR-51 | Maintenance manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. Manual to include a detailed maintenance schedule for all the planned maintenance activities over a five year period including the activity, a high-level description, ​frequency, duration and equipment status during maintenance activity. NOTE: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 5.10.2, 5.7.1 | PDF | CFIHOS-70000206
Procedures
S7141-IR-64 | Diesel generator package performance test procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document will include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements and to document the condition of the equipment as tested from factory. Test set-up and test equipment is defined. This will include engine performance test, generator load test, static load test, mechanical run test, noise test etc. Instrumentation, ECP, GCP and safety equipment will be function tested to ensure operation conforms to the cause and effect chart and full communication test of all hardwired and soft signals. Suppliers standard (routine) test procedures should be used as far as possible | 4.1 | PDF | CFIHOS-70000427
S7141-IR-65 | Painting and coating procedure | Verification of suppliers compliance with surface protection and coating requirements. This document provides a procedure for coating operator to ensure repeatability and formalism and hence prove the quality of the coating work. This document details the work process and how the defined requirements to surface treatment, application and quality control shall be met. A procedure may cover wet paint, powder coating, or metallic coatings. The document shall include reference to applied standards and the information about revision of the applied standard. Procedure to include painting system. |  | PDF | CFIHOS-70000384
Records
S7141-IR-63 | Diesel generator package performance test records | The factory acceptance test (FAT) report will be used to verify that the equipment has been tested according to FAT procedure established on the basis of ISO 8528-6:2005. The FAT report will be used for acceptance of the equipment delivery This document shall include all testing activities and their acceptance criteria specified in the approved FAT procedure and ITP. Test set-up and test equipment shall be defined. | 4.1 | PDF | CFIHOS-70000429
S7141-IR-61 | Manufacturer record book (MRB) | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and Vendor: Shall include but not be limited to documents recording compliance with statutory and/or local regulations, and inspection and testing results / reports for all the testing (e.g. Mill tests on material, production test coupon results, NDE, NDE personnel qualification, impact test, heat treatment, leak testing etc.) carried out at vendor/sub-vendor shop and at mill. Type test certificates MRB will include test results of the performance tests conducted at sub-supplier's shops like for diesel engine, generator, electric motors, etc. | 4.10, 4.7.2, 4.7.4, 4.7.5, 6.3 | PDF
S7141-IR-62 | Noise test records | Noise test reports based on the standard or plant noise acceptance test procedure, including measurement and calculation methods and tolerances. A final plant acceptance test shall be performed and reported in a noise verification report by the end-user or contractor, or by an independent party according to the test procedures agreed. Some authorities require certified or accredited organizations to be involved. The report may be prepared in accordance with the format shown in ISO 15664, Annex I. The verification report usually includes a noise survey of the plant. The results of the survey will be compared with the project requirements. The comparison of required and determined noise levels completes the verification process. The model noise survey report is not specifically intended to describe the measurement of sound pressure levels of individual items of equipment and the derivation of their sound power levels. However, while such activities may be part of the objectives of a verification report, such noise measurements are described in detail in other relevant International Standards. |  | PDF
Reports
S7141-IR-71 | Material handling report | Supplier will prepare report identifying methods of handling for disassemble and reassembly of components in the diesel generator package. The report will detail lifting methods and transportation requirements for the items of weight 25 kg or more in a safe manner. Report will include drawings/sketches indicating size of items, weight, center of gravity, frequency, special tools required, etc. Procedure for removal of major items outside the enclosure shall also be provided for the diesel generator package supplied with an enclosure. Removal of the panels of the enclosure will be identified in the drawings. | 4.9, 5.10.2 | PDF | CFIHOS-70000198
S7141-IR-70 | Type test report | The results of test performed to provide evidence that the design meets the requirements of the functional specification (See ISO 13880:1999). When specified, type test will be independently verified by a third part and supported by a Certificate of Conformance. Type test certificates for the following items will be provided: - diesel engine; - generator; - motor; - terminal box; - luminaire; - electric heater; - all electrical items included in the package; - all instrumentation items included in the package; - all bulk items. | 4.5 | PDF
Purchase Order Specific Information Requirements
`
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: