## Front & Preliminaries
|  |  |  | SPECIFICATION | September 2022
|  |  |  | IOGP S-714-1D | Version 0.1
Procurement Data Sheet for
Diesel Generator Package
(ISO/IEC Offshore)
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | September 2022 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-714-1D (0.1) Procurement Data Sheet for
Diesel Generator Package (ISO/IEC Offshore)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-714-1D (0.1) Procurement Data Sheet for
Diesel Generator Package (ISO/IEC Offshore)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of diesel generator package (ISO/IEC Offshore) in accordance with IOGP S-714-1 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet, to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-714-1), information requirements specification (IOGP S-714-1L) and quality requirements specification IOGP (S-714-1Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Procurement Data Sheet
Row | IOGP S-714-1D (0.1) Data Sheet for Diesel Generator Package (ISO/IEC Offshore) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Part 1: Application, ratings, performance, and testing of diesel generator packages
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
7 |  | Project country : | input data |  | input data
8 |  | Project region : | input data |  | input data
9 |  | Diesel generator package installation facility type : | select |  | select | [5 empty] | select | offshore floating | offshore fixed
10 |  | Diesel generator package installation environment : | select |  | select | [5 empty] | select | inside | outside with weather protection | open-air
11 |  | Diesel generator package configuration : | select |  | select | [5 empty] | select | B | C | D
12 |  | Classification society certification : | select |  | select | [5 empty] | select | ABS | BV | CCS | CRS | DNV | IRClass | KR | LR | NKK | PRS | RINA | not applicable
13 |  | Power required at generator terminals : | input data | kVA | input data | kVA
14 |  | Diesel generator package rated power factor : | 0.8 |  | 0.8 | [5 empty] | select | 0.8 | other
15 |  | a.c. generator rated voltage : | input data | V | input data | V
16 |  | a.c. generator rated frequency : | 50 | Hz | 50 | Hz |  |  |  |  | select | 50 | 60
17 |  | Start-up time - actuation of start signal to power at generator terminals : | input data | s | input data | s
18 |  | Diesel generator package power rating category : | select |  | select | [5 empty] | select | emergency standby power (ESP) | limited-time running power (LTP) | prime power (PRP) | continuous power (COP)
19 |  | Governing system performance class : | select |  | select | [5 empty] | select | G1 | G2 | G3 | G4
20 |  | Control mode : | select |  | select | [5 empty] | select | local | local plus remote | local plus remote plus automatic
21 |  | Black start feature : | select |  | select | [5 empty] | select | required | not required
22 |  | External shutdown override provision : | not required |  | not required | [5 empty] | select | required | not required
23 |  | Maximum ambient temperature : | input data | °C | input data | °C
24 |  | Minimum ambient temperature : | input data | °C | input data | °C
25 |  | Relative humidity at maximum operating temperature​ : | input data | % | input data | %
26 |  | Auxiliary motor - specification : | select |  | select | [5 empty] | select | IOGP S-703 | manufacturer's standard
27 |  | Auxiliary a.c. supply data : | input data |  | input data
28 |  | Utility air maximum supply pressure : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
29 |  | Utility air minimum supply pressure : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
30 |  | Cooling medium supply pressure : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
31 |  | Cooling medium supply temperature : | input data | select | input data | select |  |  |  |  | select | °C | °F
32 |  | Cooling medium design pressure : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
33 |  | Cooling medium source : | input data |  | input data
34 |  | Acoustic enclosure : | select |  | select | [5 empty] | select | required | not required
35 |  | Diesel generator sound pressure level limit : | input data | dBA | input data | dBA
36 |  | Fire suppression system : | select |  | select | [5 empty] | select | water mist | CO₂ | clean agent | not required
37 |  | Installed reserve fire suppressant and propellant : | select | % | select | % |  |  |  |  | select | 0 | 100 | 200
38 |  | Lighting level inside enclosure : | 20 | lx | 20 | lx |  |  |  |  | select | 20 | 50 | 100 | 200
39 |  | Number of gas detectors : | input data |  | input data
40 |  | Gas detector model : | input data |  | input data
41 |  | Number of fire detectors : | input data |  | input data
42 |  | Fire detector model : | input data |  | input data
43 |  | Acoustic enclosure material of construction : | select |  | select | [5 empty] | select | SS 316L | supplier standard | not applicable
44 |  | Maximum sound pressure level of diesel generator - without noise enclosure : | input data | dBA | input data | dBA
45 |  | Atmospheric corrosivity category : | select |  | select | [5 empty] | select | medium corrosivity (C3) | high corrosivity (C4) | very high corrosivity (C5) | extreme corrosivity (CX)
46 |  | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
47 |  | Duration of fire integrity of the enclosure : | 60 | min | 60 | min
48 |  | Blast over pressure : | input data | kPa | input data | kPa
49 |  | Part 2: Engines
50 |  | Diesel fuel specification : | select |  | select | [5 empty] | select | ASTM D975 Grade 2D | EN 590 | other
51 |  | Diesel fuel heating value - LHV : | input data | kJ/kg | input data | kJ/kg
52 |  | Specific fuel consumption at 100 % load at site condition : | input data | kg/kW⋅h | input data | kg/kW⋅h
53 |  | Air inlet shut-off valve : | select |  | select | [5 empty] | select | required | not required
54 |  | Service power : | input data | kW | input data | kW
55 |  | Exhaust emission limits - regulation : | select |  | select | [5 empty] | select | IMO Tier II | IMO Tier III | EU Stage V | EPA Tier 4
56 |  | Type of primary starting system : | select |  | select | [5 empty] | select | electric | pneumatic | hydraulic
57 |  | Type of secondary starting system : | select |  | select | [5 empty] | select | electric | pneumatic | hydraulic | not applicable
58 |  | Battery monitoring and protection : | select |  | select | [5 empty] | select | required | not required
59 |  | Battery isolator enclosure type : | select |  | select | [5 empty] | select | industrial | Ex d
60 |  | Battery charging source : | select |  | select | [5 empty] | select | alternator-fed | external a.c. supply | alternator-fed and a.c. external supply
61 |  | Pneumatic starting system type : | select |  | select | [5 empty] | select | pneumatic starter motor | direct injection
62 |  | Pneumatic source : | select |  | select | [5 empty] | select | starting air compressor | purchaser utility system | purchaser process gas | bottle rack
63 |  | Minimum pneumatic starting pressure : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
64 |  | Pneumatic starting flow rate : | input data | select | input data | select |  |  |  |  | select | m³/h | cfm
65 |  | Air vessel design pressure : | input data | select | input data | select |  |  |  |  | select | kPa (ga) | psig
66 |  | Air vessel capacity : | input data | select | input data | select |  |  |  |  | select | m³ | ft³
67 |  | Air vessel design standard : | select |  | select | [5 empty] | select | ASME BPVC Section VIII | EN 13445 | other
68 |  | Air vessel certification : | select |  | select | [5 empty] | select | ASME code stamp | PED | other
69 |  | Hydraulic charge pump : | select |  | select | [5 empty] | select | manual pump | motor driven pump | engine driven pump | dual charge pump arrangement | not required
70 |  | Hydraulic accumulator design standard : | select |  | select | [5 empty] | select | ASME BPVC Section VIII Div. 1 | EN 13445 | other
71 |  | Hydraulic accumulator certification : | select |  | select | [5 empty] | select | ASME code stamp | PED | other
72 |  | Diesel fuel storage tank running time at 100 % load : | input data | h | input data | h
73 |  | Diesel fuel tank material : | select |  | select | [5 empty] | select | 316 stainless steel | carbon steel
74 |  | Diesel fuel day tank automatic filling system : | select |  | select | [5 empty] | select | required | not required
75 |  | Exhaust gas spark arrestor : | select |  | select | [5 empty] | select | required | not required
76 |  | Part 3: Alternating current generators
77 |  | a.c. generator type : | synchronous |  | synchronous | [5 empty] | select | asynchronous | synchronous
78 |  | Generator speed : | input data | r/min | input data | r/min
79 |  | Generator manufacturer : | input data |  | input data
80 |  | Generator model : | input data |  | input data
81 |  | Generator duty : | S1 |  | S1 | [5 empty] | select | S1 | S10
82 |  | Generator rated current : | input data | A | input data | A
83 |  | Generator efficiency at 100 % load : | input data | % | input data | %
84 |  | Stator connection type : | select |  | select | [5 empty] | select | star | delta
85 |  | Generator output connections : | select |  | select | [5 empty] | select | 3-phase 3-wire | 3-phase 4-wire
86 |  | System neutral earthing : | select |  | select | [5 empty] | select | solid | floating | resistance
87 |  | Separate neutral terminal box : | select |  | select | [5 empty] | select | required | not required
88 |  | Removable copper link between earth terminal and neutral terminal : | select |  | select | [5 empty] | select | required | not required
89 |  | Stator winding pitch : | input data |  | input data
90 |  | Generator ingress protection : | select |  | select | [5 empty] | select | IP23 | IP44 | IP55
91 |  | Terminal box ingress protection : | select |  | select | [5 empty] | select | IP44 | IP55
92 |  | Power terminal box mounting : | select |  | select | [5 empty] | select | left | right | top
93 |  | Differential protection current transformer (Class PS) : | select |  | select | [5 empty] | select | by purchaser | by supplier | not required
94 |  | Instrumentation and junction box - ingress protection : | select |  | select | [5 empty] | select | IP55 | IP56 | IP65 | IP66
95 |  | Generator cooling method : | select |  | select | [5 empty] | select | IC611 (CACA) | IC81W (CACW)
96 |  | Generator stator winding insulation thermal class and temperature rise : | select |  | select | [5 empty] | select | Class F temperature rise Class B | Class H temperature rise Class F
97 |  | Available short circuit current at point of connection : | input data | kA | input data | kA
98 |  | Generator short circuit current rating time : | input data | s | input data | s
99 |  | Generator winding RTD : | select |  | select | [5 empty] | select | required | not required
100 |  | Bearing type : | select |  | select | [5 empty] | select | rolling bearing | plain bearing
101 |  | Bearing RTDs : | select |  | select | [5 empty] | select | single | duplex | not required
102 |  | Part 4: Control panel
103 |  | Control panel location : | select |  | select | [5 empty] | select | on-skid | off-skid
104 | IOGP S-7141, 7.2, Table 1 , Table 2 | Diesel generator operation : | select |  | select | [5 empty] | select | isochronous (standalone) operation | parallel operation without grid | parallel operation without grid
105 |  | Generator synchronization : | select |  | select | [5 empty] | select | manual | automatic | manual and automatic
106 |  | Generator breaker and protection relay location : | purchaser's switchboard |  | purchaser's switchboard | [5 empty] | select | supplier's control panel | purchaser's switchboard
107 |  | Media for interface with supervisory system : | select |  | select | [5 empty] | select | hard wired discreet | serial | ethernet (Cu) | ethernet (fibre) | wireless | other | not applicable
108 |  | Protocol for interface with supervisory system : | select |  | select | [5 empty] | select | Modbus | Profinet | RS485 | other | not applicable
109 |  | Media for interface with power management system : | select |  | select | [5 empty] | select | hard wired discreet | serial | ethernet (Cu) | ethernet (fibre) | wireless | other | not applicable
110 |  | Protocol for interface with power management system : | select |  | select | [5 empty] | select | Modbus | Profinet | RS485 | other | not applicable
111 |  | Automatic voltage regulator control mode : | select |  | select | [5 empty] | select | voltage control with droop compensation | voltage control with droop compensation and PF | voltage control with droop compensation and PF and VAr
112 |  | Starting current of the largest DOL start motor : | input data | A | input data | A
113 |  | Control panel ingress protection : | select |  | select | [5 empty] | select | IP 41 (indoor) | IP55 (outdoor) | other
114 |  | Separate control power battery charger required : | select |  | select | [5 empty] | select | required | not required
115 |  | Separate control power battery charger type : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other | not required
116 |  | Separate control power battery charger arrangement : | single |  | single | [5 empty] | select | single | dual-redundant | not applicable
117 |  | Separate control power battery type : | select |  | select | [5 empty] | select | nickel-cadmium | lead-acid
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Specify the unique tag number for the equipment.
Note on C5: A functional description of the tag.
Note on C6: Select the CAS level to be applied in IOGP S-714-1Q, Annex A, (Default value - D) Default value : D
Note on C10: Refer ISO 8528-1:2018, 9.6
Note on C11: — B: with baseframe; — C: with baseframe, integrally mounted controlgear, switchgear and auxiliaries; — D: configuration as given in C with enclosure
Note on C13: Refer to ISO 8528-1:2018, 14.2 and IEC 60034-1:2022, 5.5.2.
Note on C14: Refer to IEC 60034-1:2022, 5.5.2 and 'other' power factor should be stated in the 'Additional comments' column. Default value: 0.8 Default value : 0.8
Note on C16: Default value : 50
Note on C17: The emergency generator should be capable of supplying power within 45 s according to IEC 61892-2, 4.5.1.
Note on C18: Refer to ISO 8528-1:2018, 14.3.
Note on C19: Refer to ISO 8528-5: 2018, Table 4.
Note on C21: Black start: where the stored energy system has the capability to start the prime mover without using energy from another source.
Note on C22: Default value : not required
Note on C27: Specify the voltage, number of phases and frequency of each auxiliary a.c. supply envisaged for the diesel generator package
Note on C30: Pressure reference at package battery limit.
Note on C38: Default value : 20
Note on C45: Specify the atmospheric corrosivity category in accordance with ISO 12944-2.
Note on C46: Specify the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C47: Refer to ISO 13702, Table C.6 for using passive fire protection. Default value : 60
Note on C48: Refer to ISO 8528-1, 12.7.
Note on C50: The purchaser provides fuel properties when 'other' is selected.
Note on C53: Select the air-inlet shut-off valve to prevent overspeed due to flammable gas and for overspeed shutdown.
Note on C54: Service power: power delivered under the ambient and operating conditions of an engine application. Refer to ISO ISO 15550:2016.
Note on C57: Diesel generators in emergency service always use a secondary starting system.
Note on C58: A voltmeter is usually supplied for each battery bank to monitor the condition of the batteries.
Note on C59: Select the gas group and temperature class for the Ex d battery isolator enclosure.
Note on C75: Mandatory in hazardous area.
Note on C77: Default value : synchronous
Note on C81: Default value : S1
Note on C86: If the purchaser selects 'resistance' indicate the value of the earthing resistance in ohms and the time in seconds in the 'Additional notes' column.
Note on C89: The purchaser may specify a winding pitch to match the existing system requirements e.g. circulating current, harmonics, impedance.
Note on C92: Refer to IEC 60034-7: 2020: Table 3.
Note on C95: Refer to IEC 60034-6 for generator cooling methods.
Note on C96: Refer to IEC 60085
Note on C99: Resistance temperature detector (RTD).
Note on C104: Refer to ISO 8528-3:2020, 7.
Note on C105: Refer to ISO 8528-4:2005, 6.
Note on C106: Default value : purchaser's switchboard
Note on C112: Direct on line (DOL).
Note on C113: Specify the degree of protection in the 'Additional notes' column if 'other' is selected.
Note on C115: Select the battery charger type. If 'other' is selected, specify the type in the 'Additional notes' column. If 'manufacturer's standard' is selected, the supplier confirms the type in the 'Additional notes' column. Default value : manufacturer's standard
Note on C116: Select weather the configuration of the control power battery charger is single (1x100%), dual-redundant (2x100%) or not applicable. Default value : single

## Supplement
Row |  | IOGP S-714-1D (0.1) Procurement Data Sheet for Diesel Generator Package (ISO/IEC Offshore) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
IOGP S-714-1D (0.1) Procurement Data Sheet for
Diesel Generator Package (ISO/IEC Offshore)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-714-1 Specification for Diesel Generator Package (ISO/IEC Offshore).
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft