## Front & Preliminaries
|  |  |  | SPECIFICATION | May 2023
|  |  |  | IOGP S-734D | Version 1.1
Procurement Data Sheet for
AC Uninterruptible Power Supply (UPS)
System (PIP)
Revision history
| VERSION | DATE | PURPOSE
| 1.1 | May 2023 | Issued for Public Review
| 1 | November 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-734D (1.1) Procurement Data Sheet for
AC Uninterruptible Power Supply (UPS) System (PIP)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-734D (1.1) Procurement Data Sheet for
AC Uninterruptible Power Supply (UPS) System (PIP)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of AC uninterruptible power supply (UPS) system in accordance with IOGP S-734 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-734), information requirements specification (IOGP S-734L) and quality requirements specification (IOGP S-734Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Procurement Data Sheet
Row | IOGP S-734D (1.1) Procurement Data Sheet for AC Uninterruptible Power Supply (UPS) System (PIP) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 | 1,4.1.1,4.8.2 | UPS type : | pulse-width modulated |  | pulse-width modulated | [5 empty] | select | pulse-width modulated | ferroresonant
5 | 4.1.5,Figure 1,Figure 2 | UPS configuration : | Figure 1 - single |  | Figure 1 - single | [5 empty] | select | Figure 1 - single | Figure 2 - duplicate (paralleled) | other
6 |  | Black start : | not required |  | not required | [5 empty] | select | required | not required
7 | 4.1.3 | Certification : | UL 1778 |  | UL 1778 | [5 empty] | select | UL 1778 | CSA C22.2 No. 107.3 | other
8 | 4.1.25 | Electrical installation code : | select |  | select | [5 empty] | select | NFPA 70 (NEC) | CSA 22.1 Part 1 (CEC) | other
9 | 4.1.17 | Maximum noise level : | manufacturer's standard | dBA | manufacturer's standard | dBA |  |  |  |  | select | manufacturer's standard | 75 | 70 | other
10 | 4.1.19 | Cable entry : | select |  | select | [5 empty] | select | top | bottom | top and bottom
11 | 4.1.19 | Cable gland plate : | not required |  | not required | [5 empty] | select | not required | removable gland plate | other
12 | 4.1.20,4.1.21,4.17.3 | Copper ground bus plating : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | tin plated | silver plated | manufacturer's standard
13 | 4.1.23 | Conformal PCB coating : | not required |  | not required | [5 empty] | select | not required | required
14 |  | Conformity assessment system : | D |  | D | [5 empty] | select | A | B | C | D
15 |  | Site conditions
16 | 4.2.4 | Maximum altitude : | 1000 meters (3300 feet) | select | 1000 meters (3300 feet) | select |  |  |  |  | select | 1000 meters (3300 feet) | other | select | feet | meters
17 |  | Site location : | Input data |  | Input data
18 |  | Seismic certificate : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required | required
19 | 4.2.6 | ASCE/SEI 7-16 compliant seismic design : | not required |  | not required | [5 empty] | select | not required | required
20 | 4.1.26 | Certification (marine/offshore) : | not required |  | not required | [5 empty] | select | not required | USCG/ABS | DNV | other
21 | 4.2.2 | Maximum ambient temperature : | 40°C (104°F) | select | 40°C (104°F) | select |  |  |  |  | select | 40°C (104°F) | other | select | °F | °C
22 | 4.2.2 | Minimum ambient temperature : | 0°C (32°F) | select | 0°C (32°F) | select |  |  |  |  | select | 0°C (32°F) | other | select | °F | °C
23 | 4.2.3 | Maximum relative humidity : | ≤ 95 | % | ≤ 95 | % |  |  |  |  | select | ≤ 95 | other
24 |  | Application / operating environment : | select |  | select | [5 empty] | select | onshore | offshore - fixed | offshore - floating | marine - ship | other
25 |  | Environmental contamination : | none |  | none | [5 empty] | select | none | salt-laden | H2S | salt-laden and H2S | other
26 |  | Electrical characteristics
27 | 4.3 | Power rating : | input data | select | input data | select |  |  |  |  | select | kW | kVA
28 | 4.3,Table 1 | Normal input voltage : | 480 | V | 480 | V |  |  |  |  | select | 480 | 600 | other
29 | 4.3 | Input phase : | 3 |  | 3 | [5 empty] | select | 1 | 3
30 | 4.3 | Input frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 50 | 60
31 |  | Supply system grounding : | wye resistance grounded |  | wye resistance grounded | [5 empty] | select | wye high-resistance grounded | wye solidly grounded | wye ungrounded | delta
32 | 4.3 | Input current harmonics (THD) : | ≤ 35 | % | ≤ 35 | % |  |  |  |  | select | ≤ 35 | other
33 | 4.15.3,4.16.2 | Input system available fault current : | input data | kA | input data | kA
34 | 4.3,Table 1 | Bypass source voltage : | 480 | V | 480 | V |  |  |  |  | select | 480 | 600 | other
35 | 4.3 | Bypass phase : | 3 |  | 3 | [5 empty] | select | 1 | 3 | 3+N
36 | 4.15.3,4.16.2,4.19.3.4 | Bypass system available fault current : | input data | kA | input data | kA
37 | 4.3 | Output voltage : | 120 | V | 120 | V |  |  |  |  | select | 120 | 120/208Y | 120/240 | other
38 | 4.1.20 | Output system grounding : | select |  | select | [5 empty] | select | not required | required
39 |  | Load characteristics
40 | 4.3 | Linear load : | input data | % | input data | %
41 | 4.3 | Non-linear load : | input data | % | input data | %
42 | 4.3 | Motor load : | input data | select | input data | select |  |  |  |  | select | hp | kW
43 |  | Load power factor : | 0.8 | pf | 0.8 | pf |  |  |  |  | select | 0.8 | 1 | other
44 |  | Overall system efficiency
45 | 4.20.1 | Minimum weighted UPS efficiency : | input data | % | input data | %
46 |  | Full load heat rejection rate : | input data | BTU/HR | input data | BTU/HR
47 |  | Isolation and bypass transformers
48 | 4.5.1 | Input isolation transformer : | required |  | required | [5 empty] | select | not required | required
49 | 4.5.1,4.5.7,Figure 1,Figure 2 | Location of UPS input isolation transformer : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | integral | external
50 | 4.5.6 | External input isolation transformer k-factor rating : | K-4 |  | K-4 | [5 empty] | select | K-4 | other
51 | 4.5.2 | Bypass isolation transformer : | required |  | required | [5 empty] | select | not required | required
52 | Figure 1,Figure 2 | Location of bypass isolation transformer : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | integral | external
53 | 4.5.6 | Bypass isolation transformer k-factor rating : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
54 |  | Rectifier/charger
55 | 4.3,4.6.1 | Recharging time : | 8 | hrs | 8 | hrs |  |  |  |  | select | 8 | other
56 | 4.6.1 | Duplicate rectifier/charger : | not required |  | not required | [5 empty] | select | required | not required
57 | 4.6.1 | Temperature compensated battery charging and sensor : | select |  | select | [5 empty] | select | not required | required
58 | 4.18.1 | Bi-directional rectifier : | not required |  | not required | [5 empty] | select | required | not required
59 |  | Inverter
60 | 4.7.4 | Inverter turn-off voltage : | input data | Vdc | input data | Vdc
61 |  | Remote maintenance bypass switch
62 | 4.10.1,4.10.5,4.4.6 | Remote maintenance bypass switch location : | separate enclosure |  | separate enclosure | [5 empty] | select | separate enclosure | adjacent enclosure
63 | 4.10.4,Figure 1,Figure 2 | Bypass input circuit breaker (CB5 Figure 1 or Figure 2) : | required |  | required | [5 empty] | select | required | not required
64 | 4.10.4,Figure 1,Figure 2 | Bypass AC output circuit breaker (CB6 Figure 1 or Figure 2) : | not required |  | not required | [5 empty] | select | required | not required
65 |  | Inverter test load connection
66 | 4.11.1,Figure 1,Figure 2 | Test load terminals : | not required |  | not required | [5 empty] | select | not required | readily accessible terminals
67 |  | Battery disconnect
68 | 4.1.9,4.12.1,Figure 1,Figure 2 | Internal battery disconnect (CB3 - Figure 1, 2) : | circuit breaker |  | circuit breaker | [5 empty] | select | not required | circuit breaker | fused switch
69 | 4.1.9,Figure 1,Figure 2 | External battery disconnect (CB4 - Figure 1, 2) : | not required |  | not required | [5 empty] | select | not required | circuit breaker | fused switch
70 |  | Battery under-voltage protection : | not required |  | not required | [5 empty] | select | not required | required
71 | 4.12.1 | Battery shunt trip (ESD) : | not required |  | not required | [5 empty] | select | not required | internal disconnect | external disconnect
72 |  | External battery disconnect (area classification) : | select |  | select | [5 empty] | select | unclassified | classified
73 |  | Batteries
74 | 4.13.3,Figure 1,Figure 2 | Batteries : | required |  | required | [5 empty] | select | required | not required
75 |  | Battery type : | select |  | select | [5 empty] | select | lead acid valve regulated (VRLA) - AGM | lead acid valve regulated (VRLA) - gel | lead acid vented | nickel cadmium - partial gas recombination | nickel cadmium vented | lithium iron phosphate | other
76 |  | Battery configuration : | select |  | select | [5 empty] | select | 1 x 100 % | 2 x 100 % | not applicable | other
77 |  | Battery sizing standard : | select |  | select | [5 empty] | select | IEEE 1184 | lithium iron phosphate (consult battery manufacturer) | other
78 |  | Battery performance standard : | select |  | select | [5 empty] | select | IEC 60896-22 (valve-regulated lead-acid) | IEC 60896-11 (vented lead-acid) | IEC 62259 (nickel cadmium - partial gas recombination) | IEC 60623 (vented nickel cadmium) | IEC 62620 (lithium iron phosphate - consult battery manufacturer) | other
79 |  | Battery design life : | 10 | years | 10 | years |  |  |  |  | select | 10 | 20 | other
80 |  | Duty cycle description/diagram : | not provided - see 'Continuous load' and 'Backup time' |  | not provided - see 'Continuous load' and 'Backup time' | [5 empty] | select | attached diagram | see 'Supplement' tab - tabular form | not provided - see 'Continuous load' and 'Backup time' sections
81 |  | Continuous load : | input data | kW | input data | kW
82 |  | Backup time : | 30 | minutes | 30 | minutes |  |  |  |  | select | 30 | 60 | 120 | other
83 |  | Battery design margin : | 1 |  | 1 | [5 empty] | select | 1 | 1.1 | 1.15 | other
84 |  | Battery aging factor : | 1.25 |  | 1.25 | [5 empty] | select | 1.25 | other
85 |  | Battery rated capacity : | input data | Ah | input data | Ah
86 |  | Nominal battery string DC voltage : | input data | V | input data | V
87 | 4.14.12 | Battery mounting : | rack mount |  | rack mount | [5 empty] | select | rack mount | cabinet - adjacent to UPS | cabinet - remote from UPS | battery box | other
88 |  | Remote battery cabinet lockable : | not applicable for rack mount |  | not applicable for rack mount | [5 empty] | select | required | not required | not applicable for rack mount
89 |  | Battery spill containment : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | corrosion resistant tray | absorbent pad | not required
90 |  | Battery location (area classification) : | select |  | select | [5 empty] | select | unclassified | classified (CID2 Group B) | classified (Zone 2 Group IIC) | other
91 |  | Battery location (ambient temperature) : | 77 ºF (25 ºC) | select | 77 ºF (25 ºC) | select |  |  |  |  | select | 77 ºF (25 ºC) | other | select | ºF | ºC
92 |  | Deferred delivery : | not required |  | not required | [5 empty] | select | required | not required
93 |  | AC panelboard
94 |  | AC distribution panelboard : | not required |  | not required | [5 empty] | select | required | not required
95 |  | Certification : | not applicable |  | not applicable | [5 empty] | select | UL 67 | CSA 22.2 No. 29 | other | not required | not applicable
96 |  | Enclosure type : | not applicable |  | not applicable | [5 empty] | select | NEMA 1 | NEMA 1 gasketed | not applicable | other
97 |  | Number of AC circuits : | input data |  | input data
98 | 4.1.24 | Main circuit breaker : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required | required
99 | 4.1.24 | Branch circuit protection : | not applicable |  | not applicable | [5 empty] | select | not applicable | circuit breakers | fuses | fuse and circuit breaker combination
100 |  | UPS enclosure
101 | 4.14.1 | Enclosure NEMA rating : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | NEMA 1 | NEMA 1 gasketed | other
102 | 4.14.11 | Enclosure finish : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
103 | 4.14.3 | Lifting base : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required | not required
104 | 4.14.4 | UPS enclosure access : | front access only |  | front access only | [5 empty] | select | front access only | front and rear access
105 |  | Enclosure accessibility : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | via tools | lock and key
106 | 4.14.7 | Cooling fans replaceable when UPS on-line : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | required | not required | manufacturer's standard
107 | 4.14.10 | Air inlet dust filters : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required | not required
108 | 4.14.13 | UPS enclosure(s) temperature sensor : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required | not required
109 |  | Controls monitoring and communications
110 | 4.18.1 | On-line battery capacity testing into the load : | not required |  | not required | [5 empty] | select | not required | automatic | manual
111 | 4.1.15,4.18.3.1,4.19.1,4.6.2 | Mimic screen : | HMI |  | HMI | [5 empty] | select | manufacturer's standard | HMI | LED - indicators and meters
112 | 4.1.15,4.1.22,4.18.2.1,4.18.2.2,4.18.2.4 | Status indication : | HMI integrated |  | HMI integrated | [5 empty] | select | HMI integrated | manufacturer's standard | discrete LED
113 | 4.18.2.4,4.18.4.2 | Additional indication and alarms : | not required |  | not required | [5 empty] | select | not required | required
114 | 4.18.3.2 | Meters : | HMI integrated |  | HMI integrated | [5 empty] | select | HMI integrated | digital meter | analog meter
115 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface media for ECMS : | not required |  | not required | [5 empty] | select | not required | hardwired discrete | serial | Ethernet (Cu) | Ethernet (fiber) | wireless | other
116 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface protocol for ECMS : | not applicable |  | not applicable | [5 empty] | select | not applicable | potential free contact | RS485 | Modbus TCP/IP | Profinet | Ethernet IP | other
117 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface network redundancy for ECMS : | not required |  | not required | [5 empty] | select | not required | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
118 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | UPS remote access (via interface for ECMS) : | not required |  | not required | [5 empty] | select | not required | required - read only | required - read/write
119 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface media for PCS : | not required |  | not required | [5 empty] | select | not required | hardwired discrete | other
120 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface protocol for PCS : | not applicable |  | not applicable | [5 empty] | select | not applicable | potential free contact | RS485 | Modbus TCP/IP | Profinet | Ethernet IP | other
121 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface media for SIS / ESD and FGS to UPS : | not required |  | not required | [5 empty] | select | not required | form-C dry contact
122 | 4.18.7.1,4.18.7.2,4.18.7.3,4.20.11,Figure 3 | Interface media for SIS / ESD and FGS to battery isolator : | not required |  | not required | [5 empty] | select | not required | form-C dry contact
123 |  | Tagging and nameplates
124 | 4.19.4 | Additional nameplate information : | not required |  | not required | [5 empty] | select | required | not required
125 |  | Inspection and testing
126 | 4.20.10 | Full rated capacity burn in test : | not required |  | not required | [5 empty] | select | not required | required - manufacturer's standard duration | required - other duration
127 |  | Battery capacity test (SAT) : | not required |  | not required | [5 empty] | select | required | not required
128 |  | Shipping
129 | 4.21.1 | Packaging : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
130 |  | Miscellaneous
131 |  | Specialty tools : | required |  | required | [5 empty] | select | required | not required
Public Review Draft
Note on C4: Select the UPS type. Default value : pulse-width modulated
Note on C5: Select the UPS configuration. Duplicate (paralleled) UPSs are connected to the common output. If 'other' is selected, specify in the 'Additional notes' column. Default value : Figure 1 - single
Note on C6: Select whether black start is required. Black start provides capability for the UPS to start up using the connected batteries only. Normally power is required at the input to start the UPS. If that power is unavailable Black start capability is required. Default value : not required
Note on C7: Select the required certification. If 'other' is selected, enter specify the required certification in the 'Additional notes' column. Default value : UL 1778
Note on C8: Select the local installation code for scopes external to the UPS. If 'other' is selected, specify the installation code in the 'Additional notes' column.
Note on C9: Select the maximum noise level at 1 meter (3 feet). If 'other' is selected, specify in the 'Additional notes' column. Default value : manufacturer's standard
Note on C10: Select the input and output cable entry.
Note on C11: Select whether a cable gland plate is required. If pre-drilled holes or a non-magnetic plate is needed use the 'Additional notes' column for additional information. If 'other' is selected, indicate the cable entry means in the 'Additional notes' column. Default value : not required
Note on C12: Select the copper ground bus plating type. Default value : manufacturer's standard
Note on C13: Select whether conformal PCB coating is required. Default value : not required
Note on C14: Select the CAS level to be applied in IOGP S-734Q, Annex A. The criticality of the UPS service may require a higher CAS level. Default value : D
Note on C16: Specify the site maximum altitude. If 'other' is selected, specify in the 'Additional notes' column. Default value : 1000 meters (3300 feet)
Note on C17: Specify whether the seismic design is required. Specify the site physical address or latitude and longitude to determine the seismic acceleration.
Note on C18: Select whether the seismic certificate by a third party is required. Default value : not applicable
Note on C19: Select whether the seismic design is required per ASCE/SEI 7-16. Purchaser to include the seismic design basis / requirements reference document number within the 'Additional notes' column. Default value : not required
Note on C20: Select the marine/offshore certification requirements. If 'other' is selected, provide the additional certification in the 'Additional notes' column. Default value : not required
Note on C21: Specify the maximum ambient temperature. If 'other' is selected, specify in the 'Additional notes' column. Default value : 40°C (104°F)
Note on C22: Specify the minimum ambient temperature. If 'other' is selected, specify in the 'Additional notes' column. Default value : 0°C (32°F)
Note on C23: Specify the maximum relative humidity. If 'other' is selected, specify in the 'Additional notes' column. Default value : ≤ 95
Note on C24: Select the operating environment for the AC UPS. If 'marine - ship' or 'offshore - floating' is selected, use the 'Additional notes' column for the UPS design requirements (e.g., vessel pitch and roll).
Note on C25: Select the contaminant exposure to the AC UPS. If 'other' is selected, specify the contaminant exposure in the 'Additional notes' column. Default value : none
Note on C27: Specify the UPS power rating. kW is more commonly used for smaller UPS units and kVA for larger units.
Note on C28: Select the rated primary input source voltage. If 'other' is selected, specify the value in the 'Additional notes' column. Default value : 480
Note on C29: Select the number of phases for the input power supply. If an input neutral is provided or required, specify in the 'Additional notes' column. Default value : 3
Note on C30: Select the input voltage frequency. Default value : 60
Note on C31: Select the supply system grounding configuration. Default value : wye resistance grounded
Note on C32: Specify the input current total harmonic distortion. If 'other' is selected, specify the value in the 'Additional notes' column. Default value : ≤ 35
Note on C33: Specify the input available system fault current level.
Note on C34: Select the input voltage for the bypass source. If 'other' is selected, specify the value in the 'Additional notes' column. Default value : 480
Note on C35: Select the number of phases for the bypass power supply. Default value : 3
Note on C36: Specify the bypass system available fault current level.
Note on C37: Select the output voltage. For larger UPS systems, it may be more economical to select 3 phase output. Default value : 120
Note on C38: Select whether the output system grounding is required. Output system grounding can be provided in the UPS enclosure or in the remote maintenance bypass enclosure. Only one grounding point should be used.
Note on C40: Specify the linear load percentage. Total load (linear, non-linear and motor) not to exceed 100%. As an alternative, the purchaser to provide the load list to the supplier.
Note on C41: Specify the non-linear load percentage. Total non-linear load to account for motor inrush currents. Total load (linear and non-linear and motor) not to exceed 100%. As an alternative, purchaser to provide the load list to the supplier.
Note on C42: Specify the motor load in hp or kW. As an alternative provide load list to supplier.
Note on C43: Select the load power factor measured at full load. If other' is selected, specify the value in the 'Additional notes' column. Specifying a 0.8pf can result in the battery having 20% less capacity than 1.0pf. Default value : 0.8
Note on C45: Specify the value of minimum weighted UPS efficiency in accordance with the overall weighted efficiency as per IEC 62040-3:2021, Section I.3.
Note on C46: Specify the full load heat rejection rate.
Note on C48: Select whether the input isolation transformer is required. Default value : required
Note on C49: Select the location of the UPS input isolation transformer. Typically, suppliers provide integral input isolation transformers as standard. 'Integral' can mean internal to the UPS in a dedicated adjacent cabinet. Default value : manufacturer's standard
Note on C50: Specify the external input isolation transformer k-factor rating. If 'other' is selected, specify in the 'Additional notes' column. Default value : K-4
Note on C51: Select whether the bypass isolation transformer is required. A bypass transformer provides both galvanic isolation and voltage transformation. Default value : required
Note on C52: Select the location of bypass isolation transformer. Default value : manufacturer's standard
Note on C53: Select the bypass isolation transformer k-factor rating. The transformer should be capable of withstanding the heating effects of non-linear loads. If 'other' is selected, specify in the 'Additional notes' column. Default value : manufacturer's standard
Note on C55: Specify the recharging time. The recharging time to 90% of full battery capacity should be within 10 times the discharge time of the battery and typically not greater than 8 hours. If 'other' is selected, specify in the 'Additional notes' column. Default value : 8
Note on C56: Select whether the duplicate (parallel) rectifier/charger is required. Default value : not required
Note on C57: Select whether the temperature compensated battery charging and sensor is required. Temperature compensation is typically required when the batteries are not in the same ambient temperature as the UPS and is recommended for VRLA battery applications.
Note on C58: Select whether a bi-directional rectifier is required. Select this feature (active front end) if the battery is to be discharged and fed back into the source supply. Default value : not required
Note on C60: Specify the inverter turn-off voltage. If the UPS and batteries are supplied together, the supplier inputs the selection, otherwise the purchaser provides input.
Note on C62: Select the remote maintenance bypass switch location. Locating maintenance bypass switch in a separate enclosure capable of being locked in any position for supply isolation ensures safety for maintenance personnel during AC UPS maintenance. Default value : separate enclosure
Note on C63: Select whether the bypass input circuit breaker (CB5) is required as per Figure 1 or Figure 2, or purchaser's provided single line diagram. Default value : required
Note on C64: Select whether the bypass AC output circuit breaker (CB6) is required as per Figure 1 or Figure 2 or purchaser's provided single line diagram. Default value : not required
Note on C66: Select the test load connection requirement. This provides a set of readily accessible terminals to land customer cables to connect to an external circuit breaker or a fused/non-fused disconnect switch. Default value : not required
Note on C68: Select the requirement for the battery disconnect (CB3) internal to the UPS. Default value : circuit breaker
Note on C69: Select the requirement for the battery disconnect (CB4) external to the UPS. Default value : not required
Note on C70: Select whether the battery under-voltage protection is required. This can be selected to isolate battery on minimum voltage or to prevent damage to the battery. This applies only if an 'internal battery disconnect' is selected. Default value : not required
Note on C71: Select the battery shunt trip (ESD). The battery shunt trip can be selected to provide battery isolation on emergency shutdown (ESD). Selecting 'internal disconnect' may result in added complexity and additional cost. Default value : not required
Note on C72: Select the external battery disconnect (area classification). If 'classified' is selected, Class/Div/Zone and gas group to be added in the 'Additional notes' column.
Note on C74: Select whether the batteries are required. Default value : required
Note on C75: Select the battery type suitable for the application and the environment.
Note on C76: Select the configuration of the battery. If 'other' is selected, specify the required configuration in the 'Additional notes' column. 1 x 100 % is typically selected with Figure 1 configuration. 2 x 100 % is typically selected with Figure 2 configuration.
Note on C77: Select the battery sizing standard based upon the battery type. If 'other' is selected, specify the battery sizing standard in the 'Additional notes' column. IEEE 1184 is typically used for lead acid and nickle-cadmium batteries.
Note on C78: Select the battery performance standard based on the battery type. If 'other' is selected, specify the battery performance standard in the 'Additional notes' column.
Note on C79: Select the design life of the batteries. The 10 year default is based on typical lead acid battery. Longer life may be achieved by selecting different battery technologies. If 'other' is selected provide the details in the 'Additional notes' column. Default value : 10
Note on C80: Select the means to calculate the battery duty cycle. Refer to IEEE 485 or IEEE 1115 for additional guidance. Default value : not provided - see 'Continuous load' and 'Backup time'
Note on C81: Specify the continuous load power if the duty cycle description/diagram is not provided.
Note on C82: Select the battery backup time. PIP ELSAP04 defaults to a minimum of 30 minutes (Section 4.13.2) which may be insufficient for some applications. Default value : 30
Note on C83: Select the battery design margin. Design margin (as used in battery sizing standards) is used to allow for future growth and less than optimum operating conditions. If 'other' is selected, specify the value in the 'Additional notes' column. Default value : 1.00
Note on C84: Specify the battery aging factor to maintain battery capacity throughout its service life. If 'other' is selected, specify in the 'Additional notes' column. Default value : 1.25
Note on C85: Specify the battery rated capacity. Purchaser to specify the battery rated capacity (for information) in case the battery is not included in the scope.
Note on C86: Specify the nominal battery string DC voltage.
Note on C87: Select the battery installation arrangement if batteries are included in the scope. If 'other' is selected, specify the value in the 'Additional notes' column. If rack mount is selected specify maximum number of tiers. Default value : rack mount
Note on C88: Select whether the remote battery cabinet is required to be lockable. Default value : not applicable for rack mount
Note on C89: Select the battery spill containment. Spill containment is typically provided for vented lead acid batteries. Default value : manufacturer's standard
Note on C90: Select the battery location (area classification). If 'other' is selected, specify the area classification in the 'Additional notes' column.
Note on C91: Specify the ambient temperature of where the batteries are to be located. Default is typically 77 ºF (25 ºC) per industry standards for battery calculations. If 'other' is selected, specify in the 'Additional notes' column. Default value : 77 ºF (25 ºC)
Note on C92: Select whether deferred delivery is required. If a long lead time is required between the build of the UPS and the installation of the battery, indicate the length of time in the 'Additional notes' column. Default value : not required
Note on C94: Select whether the AC distribution panelboard is required. Panelboards may be standalone or integrated in the rectifier/charger cabinet. Default value : not required
Note on C95: Select the AC distribution panelboard certification standard. If 'other' is selected, specify the required certification in the 'Additional notes' column. An alternate certification may be proposed. Default value : not applicable
Note on C96: Select the enclosure type. The typical enclosure type is NEMA 1. If 'other' is selected, specify the value in the 'Additional notes' column. Default value : not applicable
Note on C97: Specify the number of AC circuits. Refer to project documents for individual circuit ratings.
Note on C98: Select whether the main circuit breaker is required. Default value : not applicable
Note on C99: Select the branch circuit protection type. Default value : not applicable
Note on C101: Select the NEMA rating for the enclosure. If 'other' is selected, specify the value in the 'Additional notes' column. Default value : manufacturer's standard
Note on C102: Select the enclosure finish type. If 'other' is selected, specify in the 'Additional notes' column. Default value : manufacturer's standard
Note on C103: Select the lifting base channel mounting requirement. Default value : manufacturer's standard
Note on C104: Select the UPS internal components access door location. Default value : front access only
Note on C105: Select the means to limit access into the UPS enclosure by qualified personnel. Default value : manufacturer's standard
Note on C106: Select whether the cooling fans are to be replaceable when UPS is online without exposure to unguarded energized components. Default value : manufacturer's standard
Note on C107: Select whether the air inlet dust filters are required. Default value : manufacturer's standard
Note on C108: Select whether the UPS the enclosure temperature sensor is required. This is typically provided for over temperature protection (i.e., loss of fan, dirty filter). Default value : manufacturer's standard
Note on C110: Select whether on-line testing is required for allowing the battery to supply the load for a specified time by blocking the rectifier. Default value : not required
Note on C111: Select the mimic display type. The graphic displays of the UPS system can be included in the HMI. LED - indicators and meters can also require the need for silkscreen or phenolic tag mimic display resulting in higher cost and less available information. Default value : HMI
Note on C112: Select the status indication type. Status indicators can be integrated into the HMI or as discrete LEDs. Discrete indicators may be desirable for critical conditions/alarms. Default value : HMI integrated
Note on C113: Select whether the additional indication and alarms are required. Specify the additional list of indications and alarms in the 'Additional notes' column. Default value : not required
Note on C114: Select whether the metering will be provided by the HMI, or provided with discrete digital or analog meters. Analog and digital metering add significant complexity to display all measurements indicated in Section 4.18.3.3. Default value : HMI integrated
Note on C115: Select the required interface media for ECMS. Network connectivity interface for time synchronization, remote access and configuration is typically via ECMS. Refer to Figure 3. If 'other' is selected, specify in the ‘Additional notes’ column. Default value : not required
Note on C116: Select the required interface protocol to the ECMS. Refer to Figure 3 for further details. If 'other' is selected, specify in the 'Additional notes' column. Default value : not applicable
Note on C117: Select the required redundancy for ECMS. The UPS interface device should facilitate network redundancy. If 'other' selected, use 'Additional notes' to specify other redundancy protocols such as the rapid spanning tree protocol (RSTP) in IEEE 802.1D. Default value : not required
Note on C118: Select the whether the UPS system needs to be accessed from a central location or a remote location through the intranet or internet. Default value : not required
Note on C119: Select the direct interface for critical / safety critical status and alarms to PCS. Refer to Figure 3 for further details. If 'other' selected, use the 'Additional notes' column to specify. Default value : not required
Note on C120: Select the required interface protocol to the PCS. Refer to Figure 3 for further details. If 'other' is selected, specify in the 'Additional notes' column. Default value : not applicable
Note on C121: Select the direct interface from an Emergency Shutdown trip and Fire and Gas system function / trip to the UPS. Refer to Figure 3 for further details. Default value : not required
Note on C122: Select the direct interface for emergency shutdown and fire and gas system trips to the battery isolator. Refer to Figure 3 for further details. Default value : not required
Note on C124: Select whether the additional nameplate information are required. Specify the additional nameplate requirements not included in Section 4.19.4; for example additional customer or project specific information in the 'Additional notes' column. Default value : not required
Note on C126: Select whether the full rated capacity burn in test is required. If required, indicate the test duration in hours in the 'Additional notes' column. Default value : not required
Note on C127: Select whether the battery capacity test during SAT is to be included in the scope of service. Default value : not required
Note on C129: Select the packaging required for shipment. Examples include weatherproof packaging, temperature and humidity limits, shock, and special crating. If 'other' is selected, specify in the 'Additional notes' column. Default value : manufacturer's standard
Note on C131: Select whether the specialty tools are required for installing, operating or maintaining the UPS or battery. Default value : required

## Supplement
Row |  | IOGP S-734D (1.1) Procurement Data Sheet for AC Uninterruptible Power Supply (UPS) System (PIP) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
IOGP S-734D (1.1) Procurement Data Sheet for
AC Uninterruptible Power Supply (UPS) System (PIP)
Guidance on the use of this procurement data sheet
To be used in conjunction with :
IOGP S-734 Supplementary Specification to PIP ELSAP04 for AC Uninterruptible Power Supply (UPS) System.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft