## Front & Preliminaries
|  |  |  | SPECIFICATION | August 2024
|  |  |  | IOGP S-703D | Version 1.1
Procurement Data Sheet for
Low-voltage Three-phase Cage
Induction Motors (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 1.1 | August 2024 | Issued for Public Review
| 1 | March 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-703D (1.1) Procurement Data Sheet for
Low-voltage Three-phase Cage Induction Motors (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-703D (1.1) Procurement Data Sheet for
Low-voltage Three-phase Cage Induction Motors (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of low-voltage three-phase cage induction motors in accordance with IOGP S-703 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-703), information requirements specification (IOGP S-703L) and quality requirements specification (IOGP S-703Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Single-speed Motor
Row | IOGP S-703D (1.1) Procurement Data Sheet for Low-voltage Three-phase Cage Induction Motors (IEC) Single-speed Motor | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine - coastal | subsea | buried | onshore
11 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
12 |  | Manufacturer : | input data |  | input data
13 |  | Model number : | input data |  | input data
14 |  | Number of poles : | select |  | select | [5 empty] | select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 | 11.4.2.3.1 | Frame size/designation : | input data |  | input data
16 |  | Site conditions
17 | 6.1 | Location environment : | select |  | select | [5 empty] | select | indoor | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine - ship | other
18 | 6.1,6.2 | Altitude : | 1 000 or below | m | 1 000 or below | m |  |  |  |  | select | 1 000 or below | other
19 | 6.1,6.3 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | other
20 | 6.1,6.4 | Minimum ambient air temperature : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
21 | 6.1 | Chemicals or corrosives : | input data |  | input data
22 | 6.1 | Unusual service conditions : | no |  | no | [5 empty] | select | yes | no
23 |  | Motors rated for use in hazardous areas
24 | 11.4.11.1.1,11.4.11.1.2 | Hazardous area zone classification : | select |  | select | [5 empty] | select | zone 1 | zone 2 | zone 21 | zone 22 | non-hazardous
25 | 11.4.11.1.1,11.4.11.1.2 | Hazardous area equipment certification : | select |  | select | [5 empty] | select | ATEX | IECEx | other | not applicable
26 | 11.4.11.1.1,11.4.11.1.2 | Temperature class : | select |  | select | [5 empty] | select | T3 | T4 | T5 | T6 | T1 | T2 | not applicable
27 | 11.4.11.1.1,11.4.11.1.2 | Gas/dust group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | not applicable
28 | 11.4.11.1.1,11.4.11.1.2,11.4.11.2 | Equipment protection level : | select |  | select | [5 empty] | select | EPL Ga | EPL Gb | EPL Gc | EPL Da | EPL Db | EPL Dc | not applicable
29 | 11.4.11.1.1,11.4.11.1.2,11.4.11.2 | Type of protection : | select |  | select | [5 empty] | select | Ex db | Ex db eb | Ex eb | Ex ec | Ex tb | Ex tc | not applicable
30 |  | Driven equipment interface
31 | 4.1,4.2.1,4.2.10,4.2.2,4.2.3,4.2.4,4.2.5,4.2.6,4.2.7,4.2.8,4.2.9,5.3 | Duty type : | S1 |  | S1 | [5 empty] | select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10
32 | 10.4.2 | Direction of rotation : | select |  | select | [5 empty] | select | clockwise (cw) | counter clockwise (ccw)
33 |  | Driven equipment type : | select |  | select | [5 empty] | select | centrifugal pump | centrifugal fan | centrifugal compressor | reciprocating pump | reciprocating compressor | positive displacement pump | other
34 |  | Load drive : | select |  | select | [5 empty] | select | direct coupled | gearbox | other
35 | 11.4.7.5,Table 25 | External radial loading on motor shaft end : | input data | N | input data | N
36 | 11.4.7.5,Table 25 | External axial loading on motor shaft end : | input data | N | input data | N
37 |  | Moment of inertia of load (Jext) : | input data | kg·m² | input data | kg·m²
38 |  | Electrical operating conditions
39 | 11.3.1.2 | Motor rated voltage : | select | V | select | V |  |  |  |  | select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
40 | 11.3.1.2,7.4 | Maximum voltage variation : | select | % | select | % |  |  |  |  | select | 5 | other
41 | 11.3.1.2,7.4 | Minimum voltage variation : | select | % | select | % |  |  |  |  | select | -5 | other
42 | 7.1 | Motor rated frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
43 | 7.4 | Maximum frequency variation : | select | % | select | % |  |  |  |  | select | 2 | other
44 | 7.4 | Minimum frequency variation : | select | % | select | % |  |  |  |  | select | -2 | other
45 |  | Thermal performance
46 |  | Insulation class : | F |  | F | [5 empty] | select | F | H
47 | 8.1 | Temperature rise class : | B |  | B | [5 empty] | select | B | F
48 |  | Starting performance
49 |  | Starting designation : | N |  | N | [5 empty] | select | N | NE | NY | NEY | H | HE | HY | HEY
50 |  | Starting method : | select |  | select | [5 empty] | select | direct-on-line | star-delta | auto-transformer starter | variable speed drive | soft-starter | other
51 |  | Starting load : | select |  | select | [5 empty] | select | unloaded | loaded
52 | 11.3.1.4 | Re-acceleration with full residual voltage in total phase opposition to supply voltage : | no |  | no | [5 empty] | select | yes | no
53 | 11.3.1.1 | Locked rotor current required : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
54 | 11.3.1.1,Table 22 | Locked rotor current tolerance required : | 20 | % | 20 | % |  |  |  |  | select | 20 | 10 | 0
55 | 11.3.1.1,Table 22 | Locked rotor current at rated voltage : | input data | pu of FLC | input data | pu of FLC
56 | 11.3.1.1 | Locked rotor current at 80 % of rated voltage : | input data | pu of FLC | input data | pu of FLC
57 | 9.5,Table 22 | Pull-up torque : | input data | pu of full load torque | input data | pu of full load torque
58 | Table 22 | Locked rotor torque at rated voltage : | input data | N·m | input data | N·m
59 |  | Locked rotor torque at 80 % of rated voltage : | input data | N·m | input data | N·m
60 |  | Locked rotor power factor at rated voltage : | input data |  | input data
61 | Table 22 | Moment of inertia of the rotor (Jm) : | input data | kg·m² | input data | kg·m²
62 |  | Maximum permissible starting time at rated voltage : | input data | s | input data | s
63 |  | Maximum permissible starting time at 80 % of rated voltage : | input data | s | input data | s
64 |  | Operating performance
65 | 5.5.3 | Rated output : | input data | kW | input data | kW
66 |  | Rated current : | input data | A | input data | A
67 | Table 22 | Rated speed : | input data | min⁻¹ | input data | min⁻¹
68 |  | Rated torque : | input data | N·m | input data | N·m
69 |  | Rated breakdown torque : | input data | pu | input data | pu
70 | 5.9.1,5.9.2 | Efficiency category : | IE3 |  | IE3 | [5 empty] | select | IE3 | IE4 | other
71 | 5.9.1,5.9.2,Table 22 | Efficiency at rated output : | input data | % | input data | %
72 |  | Efficiency at 75 % of rated output : | input data | % | input data | %
73 |  | Efficiency at 50 % of rated output : | input data | % | input data | %
74 | Table 22 | Power factor at rated output : | input data | pu | input data | pu
75 |  | Power factor at 75 % of rated output : | input data | pu | input data | pu
76 |  | Power factor at 50 % of rated output : | input data | pu | input data | pu
77 |  | Surface protection
78 | 11.4.2.4.1,11.4.2.4.2 | Surface protection corrosivity category : | C3 |  | C3 | [5 empty] | select | C3 | C4 | C5 | CX
79 | 11.4.2.4.3 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
80 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
81 |  | Motor construction
82 | 6.8.1,Table 23 | Motor enclosure ingress protection : | IP55 |  | IP55 | [5 empty] | select | IP55 | IP56 | IP54 | IP44 | IP23 | other
83 | 11.4.3.1 | Cooling method : | IC4A1A1 |  | IC4A1A1 | [5 empty] | select | IC4A1A1 | other
84 |  | Motor weight : | input data | kg | input data | kg
85 | 11.4.2.2.1 | Mounting arrangement : | select |  | select | [5 empty] | select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | IM V1 (IM 3015) | IM V6 (IM 1035) | other
86 |  | Jacking bolts : | not required |  | not required | [5 empty] | select | not required | required
87 |  | Auxiliary terminal box for monitoring device : | not required |  | not required | [5 empty] | select | not required | required
88 |  | Fan direction of rotation : | bidirectional |  | bidirectional | [5 empty] | select | bidirectional | unidirectional clockwise | unidirectional counter clockwise
89 | 11.4.6.2 | External fan impeller material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | GRP | steel fan | other
90 |  | Hardware material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | 316L stainless steel | hot-dip galvanized | other
91 |  | Bearings
92 | 11.4.7.7 | Bearing insulation : | not required |  | not required | [5 empty] | select | only non-drive end | both drive end and non-drive end | not required
93 | 11.4.7.1,11.4.7.2,11.4.7.5,11.4.7.6,11.4.7.9,Table 25,Table 26 | Drive end bearing type : | input data |  | input data
94 | 11.4.7.1,11.4.7.2,11.4.7.5,11.4.7.6,11.4.7.9,Table 25,Table 26 | Non-drive end bearing type : | input data |  | input data
95 | 11.4.7.4 | Internal clearance : | C3 |  | C3 | [5 empty] | select | C2 | CN | C3 | C4 | C5
96 | 11.4.7.6,11.4.7.8,Table 26 | Lubrication specification : | input data |  | input data
97 | Table 25 | Thrust load on vertical motor : | input data |  | input data
98 |  | Vibration
99 |  | Vibration test : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required with rigid mounting | not required
100 | 11.4.4.1,11.4.4.3 | Applicable rotor balancing grade : | G 2,5 |  | G 2,5 | [5 empty] | select | G 2,5 | G 1,0 | manufacturer's standard
101 | 11.4.4.1,11.4.4.2,11.4.4.3 | Maximum vibration limit : | grade A - IEC 60034-14:2018 Table 1 |  | grade A - IEC 60034-14:2018 Table 1 | [5 empty] | select | grade A - IEC 60034-14:2018 Table 1 | grade B - IEC 60034-14:2018 Table 1 | other
102 |  | Sensor type for vibration measurement : | not required |  | not required | [5 empty] | select | one stainless steel shock pulse monitoring nipple per bearing | one accelerometer per bearing | other | not required
103 |  | Noise
104 | 11.3.2.1,Table 22 | Sound pressure level at no load : | IEC 60034-9 limits | dB(A) | IEC 60034-9 limits | dB(A) |  |  |  |  | select | IEC 60034-9 limits | other
105 |  | Anti-condensation heaters
106 | 11.4.9.1,11.4.9.2,5.7.1.5.1 | Anti-condensation heater : | not required |  | not required | [5 empty] | select | windings | windings and line conductor terminal box | not required
107 | 11.4.9.2 | Anti-condensation heater supply voltage (AC) : | not applicable | V | not applicable | V |  |  |  |  | select | 100-120 single phase | 200-240 single phase | not applicable
108 | 11.4.9.2,11.4.9.3 | Separate anti-condensation heater terminal box : | not applicable |  | not applicable | [5 empty] | select | required | not required | not applicable
109 | 11.4.9.3 | Warning label language : | not applicable |  | not applicable | [5 empty] | select | English | other | not applicable
110 |  | Temperature monitoring
111 | 11.4.8.1,8.6.1 | Winding temperature detection : | select |  | select | [5 empty] | select | one thermistor (PTC) per phase | two thermistors (PTCs) per phase | three wire Pt-100 | other | not required
112 |  | Terminal boxes
113 |  | Terminal box ingress protection : | IP55 |  | IP55 | [5 empty] | select | IP55 | IP56 | other
114 | 11.4.5.2 | Line conductor terminal box location viewed from drive end : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | top | right | left | bottom
115 |  | Line conductor cable quantity per phase : | input data |  | input data
116 |  | Line conductor cable type : | input data |  | input data
117 |  | Line conductor size : | select | mm² | select | mm² |  |  |  |  | select | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | other
118 | 11.4.5.3 | Line conductor terminal box cable gland entries : | input data |  | input data
119 |  | Line conductor terminal box size : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | one size above standard | two size above standard
120 |  | Miscellaneous
121 |  | Provision for IoT hardware installation : | not required |  | not required | [5 empty] | select | required | not required
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-703Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the location of the facility where the equipment will be permanently installed.
Note on C11: Select the status of the order.
Note on C12: Specify the name of the motor manufacturer.
Note on C13: Specify the model number of the motor.
Note on C14: Select the required number of poles. If "other" is selected, specify the pole requirements in "Additional notes".
Note on C15: Specify the motor frame size/designation. Where this is not specified by the purchaser, supplier to specify the frame size as per the standard offering for the application.
Note on C17: Select the location where the motor is to be situated. If "other" is selected, specify in "Additional notes".
Note on C18: This is the altitude above sea level. The IEC 60034-1 default is 1 000 m. If "other" is selected, specify the value in "Additional notes" only if the site conditions are higher than 1 000 m. Default value : 1 000 or below
Note on C19: The IEC 60034-1 default is 40 °C. Select a value different from 40 °C only if the site conditions are higher than the IEC default. "If other" is selected, specify the temperature values in "Additional notes". Default value : 40
Note on C20: Select "other" and specify the value in "Additional notes" only if the site conditions are lower than 0 °C . Default value : 0
Note on C21: Specify the chemicals or corrosives that may be present in the location environment (e.g. presence of H2S).
Note on C22: Select "yes" for unusual service conditions not covered elsewhere in IOGP S-704 such as salt-laden and abrasive dust . Specify unusual service conditions in "Additional notes". Default value : no
Note on C24: Select the hazardous area zone classification in which the motor is installed.
Note on C25: Select which certification is acceptable for motors to be located in a hazardous area. If "other" is selected, specify the certification in "Additional notes".
Note on C26: Select the temperature class for which the motor is rated for in accordance with IEC 60079.
Note on C27: Select the gas/dust group for which the motor is to be rated in accordance with IEC 60079.
Note on C28: Select the equipment protection level (EPL) in accordance with IEC 60079-14.
Note on C29: Select the type of protection for which the motor is rated for in accordance with IEC 60079.
Note on C31: Select the duty type as defined in IEC-60034-1, Clause 4. The JIP33 default is S1 for single-speed use. Default value : S1
Note on C32: Select the direction of motor shaft rotation observed while facing the drive end when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C33: Select the equipment intended to be driven by the high-voltage motor. If "other" is selected, specify details of the driven equipment in "Additional notes".
Note on C34: Select the method of power transfer to the driven equipment. Specify the load drive with details in "Additional notes". Include the gearbox data sheet when provided.
Note on C35: Purchaser to specify the maximum external radial loading where applicable. Supplier to specify the maximum permissible radial loading if not specified by the purchaser.
Note on C36: Purchaser to specify the maximum external axial loading on the shaft end where applicable. Supplier to specify the maximum permissible axial loading if not specified by the purchaser.
Note on C37: Specify the moment of inertia (MR²) of the load at the motor shaft.
Note on C39: Specify the input voltage, expressed in V, for which the motor is rated.
Note on C40: Select the maximum steady-state voltage limit as a percentage of the supply voltage. Figure 11, zone B upper Y boundary default is 1,10 pu (10 %). If "other" is selected, specify the limit requirements in "Additional notes".
Note on C41: Select the minimum steady-state voltage limit as a percentage of the supply voltage. Figure 11, zone B lower Y boundary default is 0,90 pu (-10 %). If "other" is selected, specify the limit requirements in "Additional notes".
Note on C42: Select the supply frequency for which the motor is rated.
Note on C43: Select the maximum frequency limit as a percentage of the supply frequency at which the motor provide the rated torque. If "other" is selected, specify the limit requirements in "Additional notes".
Note on C44: Select the minimum frequency limit as a percentage of the supply frequency at which the motor is to provide the rated torque. If "other" is selected, specify the limit requirements in "Additional notes".
Note on C46: Select the insulation class of motor in accordance with IEC 60085. Default value : F
Note on C47: Select the temperature rise class of motor in accordance with IEC 60085. Specify another temperature rise value in the "Additional notes" column to offset the effect of extended stopping time. Default value : B
Note on C49: Select the motor starting designation in accordance with IEC 60034-12. Where locked rotor apparent power requirements in accordance with IEC 60034-12:2016, Table 2 cannot be achieved, design NE may be selected. Default value : N
Note on C50: Select the motor starting method for which the motor is to be provided. If "other" is selected, specify the bypass requirements in "Additional notes".
Note on C51: Select the load condition as seen by the motor at starting taken from the driven equipment data sheet. Specify the load information in "Additional notes" (e.g. valve open/close, damper open/close) and provide the load curve of the driven equipment.
Note on C52: Select "yes" when the motor starter is unable to detect reconnection torques and the motor has to be able to re-accelerate with the full residual voltage in total phase opposition. Otherwise, select "no". Default value : no
Note on C53: If not a manufacturer's standard, select "other" and specify the locked rotor current required in "Additional notes", expressed as a ratio of the starting current to the rated current (Is/In). Tolerances apply over the specified locked rotor current. Default value : manufacturer's standard
Note on C54: Select the required tolerance for the locked rotor current. While the default is +20 % as per Table 22, it is acknowledged that some projects may require a more stringent value. Default value : 20
Note on C55: Specify as 'per unit' (pu) value of the full load current (Is/In) at rated voltage.
Note on C56: Specify at 80 % of rated voltage and rated frequency as 'per unit' (pu) value of the full load current (Is/In).
Note on C57: Specify the smallest steady-state asynchronous torque that the motor develops between zero speed and the speed that corresponds to the breakdown torque when the motor is supplied at 100 % of rated voltage and rated frequency.
Note on C58: Specify the smallest measured torque the motor develops at its shaft, with the rotor locked, over all its angular positions at rated voltage and rated frequency.
Note on C59: Specify the smallest measured torque the motor develops at its shaft, with the rotor locked, over all its angular positions at 80 % of rated voltage and rated frequency.
Note on C60: Specify the power factor as 'per unit' (pu) value with the rotor locked at rated voltage and rated frequency.
Note on C61: Specify the rotor moment of inertia (MR²) as defined in 3.24.
Note on C62: Specify the maximum permissible time (safe limit) that the motor can take to reach its rated speed at rated voltage while starting from 'hot' and ensure no winding failure.
Note on C63: Specify the maximum permissible time (safe limit) that the the motor can take to reach its rated speed at 80% of rated voltage while starting from 'hot' and ensure no winding failure.
Note on C65: Supplier to specify the rated output, i.e. the required motor shaft rated mechanical power, if not specified by the purchaser.
Note on C66: Specify the motor rated current while operating at rated voltage and rated frequency.
Note on C67: Specify the steady-state asynchronous rotor speed while delivering the rated output at rated voltage and rated frequency.
Note on C68: Specify the steady-state asynchronous rotor torque while delivering the rated output at rated voltage and rated frequency.
Note on C69: Specify the maximum steady-state asynchronous torque that the motor develops when the motor is supplied at rated voltage and rated frequency, expressed as per the unit value of the rated (full load) torque.
Note on C70: Select the efficiency category (IE) in accordance with IEC 60034-30-1. Default value : IE3
Note on C71: Specify the efficiency of the motor while operating at rated output.
Note on C72: Specify the efficiency of the motor while operating at 75 % of the rated output.
Note on C73: Specify the efficiency of the motor while operating at 50 % of the rated output.
Note on C74: Specify the cosine of the angle between active power and apparent power when the motor is operated at rated output.
Note on C75: Specify the cosine of the angle between active power and apparent power when the motor is operated at 75 % of the rated output.
Note on C76: Specify the cosine of the angle between active power and apparent power when the motor is operated at 50 % of the rated output.
Note on C78: Select the surface corrosivity category in accordance with ISO 12944-2, 5.1.1. Default value : C3
Note on C79: Select the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C80: Where the manufacturer's standard paint colour is unacceptable and "other" is selected, specify the paint colour requirements in "Additional notes". Default value : manufacturer's standard
Note on C82: Select the ingress protection value in accordance with IEC 60034-5. If "other" is selected, specify the motor enclosure ingress protection value in "Additional notes". Default value : IP55
Note on C83: Select the motor cooling method in accordance with IEC 60034-6. If "other" is selected, specify the motor cooling method in "Additional notes". Default value : IC4A1A1
Note on C84: Specify the fully assembled weight of the motor.
Note on C85: Select the motor mounting arrangement in accordance with IEC 60034-7.
Note on C86: Select whether jacking bolts for safe and standard means of alignment of the motor with the coupled equipment during installation is required. Default value : not required
Note on C87: Select whether a separate terminal box for monitoring device is required. Each monitoring device type will have a separate terminal block within the auxiliary terminal box. Default value : not required
Note on C88: Select the direction of rotation of fan observed while facing the drive end when connecting motor terminals U-V-W to supply L1-L2-L3. Default value : bidirectional
Note on C89: Select the material for the external fan impeller. Default value : manufacturer's standard
Note on C90: Select the hardware material for external screws, bolts, nuts, washers and any other fixings. If "other" is selected, specify the details of hardware material used for the motor enclosure in "Additional notes". Default value : manufacturer's standard
Note on C92: Select whether bearing insulation in motor is required. When both bearings are insulated, a suitable shaft grounding system may be provided on the rotor shaft. Default value : not required
Note on C93: Specify the drive end bearing type, model number and associated details.
Note on C94: Specify the non-drive end bearing type, model number and associated details.
Note on C95: Specify the required internal clearance of the bearing in accordance with ISO 5753-1. Default value : C3
Note on C96: Specify the approved (refer to 11.4.7.8) lubrication specification and associated product reference code for lubrication of re-greasable bearings.
Note on C97: Specify the the up and down thrust loads for selection of appropriate bearings for motor in vertical orientation.
Note on C99: Select whether the vibration test procedure should follow the rigid mounting method similar to that of the mounting method at installation location or adopt the manufacturer's standard method of mounting while performing the test. Default value : manufacturer's standard
Note on C100: Select the required balancing grade to determine the permissible limits for residual unbalance to achieve the vibrations grade (maximum vibration limits) Default value : G 2,5
Note on C101: Select the maximum vibration limits in accordance with IEC 60034-14:2018, Table 1. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes". Default value : grade A - IEC 60034-14:2018 Table 1
Note on C102: Select the sensor type for vibration measurement. Default value : not required
Note on C104: Select the maximum permissible motor A-weighted sound pressure level at a reference distance of 1 m at no load and rated speed. If “other”, specify value in “Additional notes”. For limits, refer to IEC 60034-9: 2021, Table 2 (50 Hz) or Table 3 (60 Hz). Default value : IEC 60034-9 limits
Note on C106: Select whether anti-condensation heaters in the motor are required. Default value : not required
Note on C107: Select the supply voltage for which the anti-condensation heater will be rated. Refer to the project specified voltage level applicable in the voltage range selected. Default value : not applicable
Note on C108: Select whether separate anti-condensation heaters terminal box for the motor are required. Default value : not applicable
Note on C109: Select the language to be used for the label warning that heater terminals may be live when the motor is isolated. When the language is other than English, specify it in "Additional notes". Default value : not applicable
Note on C111: Select the winding temperature detection as required. Where any other type of winding temperature detector is required, select "other" and specify details in "Additional notes".
Note on C113: Select the ingress protection value in accordance with IEC 60034-5 for which the terminal boxes are rated. Default value : IP55
Note on C114: Select the line conductor terminal box location when viewed from the drive end of the motor, using coding in accordance with IEC 60034-7:2020. For double ended motors, specify the requirement in "Additional notes". Default value : manufacturer's standard
Note on C115: Specify the number of runs of cable per phase.
Note on C116: Specify the line conductor cable type (e.g. single-core, multi-core, armoured, un-armoured).
Note on C117: Select the size (cross-section area) of the line conductor. Where the line conductor size is not yet determined, supplier to specify maximum size of cable acceptable into the supplied terminal box.
Note on C118: Select the number and size of cable gland entries in line terminal box (e.g. 1 x M32, 2 x M20). Where gland entry number and sizes are not yet determined, supplier to specify the terminal box cable gland entry details.
Note on C119: Select a larger than standard main terminal box as required where a higher size/rated power supply cable is anticipated. Where inappropriate for the specified cable details, supplier to select an appropriate terminal box size. Default value : manufacturer's standard
Note on C121: Select whether mounting provisions of IoT hardware provisions on the motor are required. Specify the mounting points and installation provisions in "Additional notes". IoT hardware may be procured and mounted by the purchaser at a later date. Default value : not required

## Convertor Duty Motor
Row | IOGP S-703D (1.1) Procurement Data Sheet for Low-voltage Three-phase Cage Induction Motors (IEC) Convertor Duty Motor | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | Identifier
4 |  | Tag number : | input data |  | input data
5 |  | Tag description : | input data |  | input data
6 |  | General information
7 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
8 |  | Project country : | input data |  | input data
9 |  | Project region : | input data |  | input data
10 |  | Plant environmental location : | select |  | select | [5 empty] | select | offshore | marine - coastal | subsea | buried | onshore
11 |  | Order status : | select |  | select | [5 empty] | select | for enquiry | for purchase
12 |  | Manufacturer : | input data |  | input data
13 |  | Model number : | input data |  | input data
14 |  | Number of poles : | select |  | select | [5 empty] | select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 | 11.4.2.3.1 | Frame size/designation : | input data |  | input data
16 |  | Converter manufacturer : | input data |  | input data
17 |  | Converter model number : | input data |  | input data
18 |  | Site conditions
19 | 6.1 | Location environment : | select |  | select | [5 empty] | select | indoor | onshore - coastal | onshore - desert | onshore - inland | offshore - fixed | offshore - floating | marine - ship | other
20 | 6.1,6.2 | Altitude : | 1 000 or below | m | 1 000 or below | m |  |  |  |  | select | 1 000 or below | other
21 | 6.1,6.3 | Maximum ambient air temperature : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50 | other
22 | 6.1,6.4 | Minimum ambient air temperature : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | other
23 | 6.1 | Chemicals or corrosives : | input data |  | input data
24 | 6.1 | Unusual service conditions : | no |  | no | [5 empty] | select | yes | no
25 |  | Motors rated for use in hazardous areas
26 | 11.4.11.1.1,11.4.11.1.2 | Hazardous area zone classification : | select |  | select | [5 empty] | select | zone 1 | zone 2 | zone 21 | zone 22 | non-hazardous
27 | 11.4.11.1.1,11.4.11.1.2 | Hazardous area equipment certification : | select |  | select | [5 empty] | select | ATEX | IECEx | other | not applicable
28 | 11.4.11.1.1,11.4.11.1.2 | Temperature class : | select |  | select | [5 empty] | select | T3 | T4 | T5 | T6 | T1 | T2 | not applicable
29 | 11.4.11.1.1,11.4.11.1.2 | Gas/dust group : | select |  | select | [5 empty] | select | IIA | IIB | IIC | IIIA | IIIB | IIIC | not applicable
30 | 11.4.11.1.1,11.4.11.1.2,11.4.11.2 | Equipment protection level : | select |  | select | [5 empty] | select | EPL Ga | EPL Gb | EPL Gc | EPL Da | EPL Db | EPL Dc | not applicable
31 | 11.4.11.1.1,11.4.11.1.2,11.4.11.2 | Type of protection : | select |  | select | [5 empty] | select | Ex db | Ex db eb | Ex eb | Ex ec | Ex tb | Ex tc | not applicable
32 |  | Driven equipment interface
33 | 4.1,4.2.1,4.2.10,4.2.2,4.2.3,4.2.4,4.2.5,4.2.6,4.2.7,4.2.8,4.2.9,5.3 | Duty type : | select |  | select | [5 empty] | select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10
34 | 10.4.2 | Direction of rotation : | select |  | select | [5 empty] | select | clockwise (cw) | counter clockwise (ccw)
35 |  | Driven equipment type : | select |  | select | [5 empty] | select | centrifugal pump | centrifugal fan | centrifugal compressor | reciprocating pump | reciprocating compressor | positive displacement pump | other
36 |  | Load drive : | select |  | select | [5 empty] | select | direct coupled | gearbox | other
37 | 11.4.7.5,Table 25 | External radial loading on motor shaft end : | input data | N | input data | N
38 | 11.4.7.5,Table 25 | External axial loading on motor shaft end : | input data | N | input data | N
39 |  | Moment of inertia of load (Jext) : | input data | kg·m² | input data | kg·m²
40 |  | Electrical operating conditions
41 |  | Motor rated voltage : | select | V | select | V |  |  |  |  | select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
42 | 7.1 | Motor rated frequency : | select | Hz | select | Hz |  |  |  |  | select | 50 | 60
43 |  | Thermal performance
44 |  | Insulation class : | F |  | F | [5 empty] | select | F | H
45 | 8.1 | Temperature rise class : | B |  | B | [5 empty] | select | B | F
46 |  | Starting performance
47 |  | Starting load : | select |  | select | [5 empty] | select | unloaded | loaded
48 | Table 22 | Moment of inertia of the rotor (Jm) : | input data | kg·m² | input data | kg·m²
49 |  | Operating performance
50 |  | Converter operation mode : | select |  | select | [5 empty] | select | variable torque | constant torque | constant power | other
51 | 11.4.10.1,5.5.3 | Rated output : | input data | kW | input data | kW
52 |  | Rated current : | input data | A | input data | A
53 | 11.4.10.1,Table 22 | Rated speed : | input data | min⁻¹ | input data | min⁻¹
54 | 11.4.10.1 | Maximum continuous operating speed : | input data | min⁻¹ | input data | min⁻¹
55 | 11.4.10.1 | Minimum continuous operating speed : | input data | min⁻¹ | input data | min⁻¹
56 | 11.4.10.1 | Rated torque : | input data | N·m | input data | N·m
57 |  | Rated breakdown torque : | input data | pu | input data | pu
58 | 5.9.1,5.9.2 | Efficiency category : | IE2 |  | IE2 | [5 empty] | select | IE2 | IE3 | IE4 | other
59 | 5.9.1,5.9.2,Table 22 | Efficiency at rated output : | input data | % | input data | %
60 |  | Efficiency at maximum continuous operating speed : | input data | % | input data | %
61 |  | Efficiency at minimum continuous operating speed : | input data | % | input data | %
62 |  | Efficiency at maximum continuous operating speed at maximum load torque : | input data | % | input data | %
63 | Table 22 | Power factor at rated output : | input data | pu | input data | pu
64 |  | Power factor at maximum continuous operating speed : | input data | pu | input data | pu
65 |  | Power factor at minimum continuous operating speed : | input data | pu | input data | pu
66 |  | Surface protection
67 | 11.4.2.4.1,11.4.2.4.2 | Surface protection corrosivity category : | C3 |  | C3 | [5 empty] | select | C3 | C4 | C5 | CX
68 | 11.4.2.4.3 | Surface protection durability category : | medium (M) 7 to 15 years |  | medium (M) 7 to 15 years | [5 empty] | select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
69 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
70 |  | Motor construction
71 | 6.8.1,Table 23 | Motor enclosure ingress protection : | IP55 |  | IP55 | [5 empty] | select | IP55 | IP56 | IP54 | IP44 | IP23 | other
72 | 11.4.3.1 | Cooling method : | IC4A1A1 |  | IC4A1A1 | [5 empty] | select | IC4A1A1 | other
73 |  | Motor weight : | input data | kg | input data | kg
74 | 11.4.2.2.1 | Mounting arrangement : | select |  | select | [5 empty] | select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | IM V1 (IM 3015) | IM V6 (IM 1035) | other
75 |  | Jacking bolts : | not required |  | not required | [5 empty] | select | not required | required
76 |  | Auxiliary terminal box for monitoring device : | not required |  | not required | [5 empty] | select | not required | required
77 |  | Fan direction of rotation : | bidirectional |  | bidirectional | [5 empty] | select | bidirectional | unidirectional clockwise | unidirectional counter clockwise
78 | 11.4.6.2 | External fan impeller material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | GRP | steel fan | other
79 |  | Hardware material : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | 316L stainless steel | hot-dip galvanized | other
80 |  | Bearings
81 | 11.4.7.7 | Bearing insulation : | not required |  | not required | [5 empty] | select | only non-drive end | both drive end and non-drive end | not required
82 | 11.4.7.1,11.4.7.2,11.4.7.5,11.4.7.6,11.4.7.9,Table 25,Table 26 | Drive end bearing type : | input data |  | input data
83 | 11.4.7.1,11.4.7.2,11.4.7.5,11.4.7.6,11.4.7.9,Table 25,Table 26 | Non-drive end bearing type : | input data |  | input data
84 | 11.4.7.4 | Internal clearance : | C3 |  | C3 | [5 empty] | select | C2 | CN | C3 | C4 | C5
85 | 11.4.7.6,11.4.7.8,Table 26 | Lubrication specification : | input data |  | input data
86 | Table 25 | Thrust load on vertical motor : | input data |  | input data
87 |  | Vibration
88 |  | Vibration test : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | required with rigid mounting | not required
89 | 11.4.4.1,11.4.4.3 | Applicable rotor balancing grade : | G 2,5 |  | G 2,5 | [5 empty] | select | G 2,5 | G 1,0 | manufacturer's standard
90 | 11.4.4.1,11.4.4.2,11.4.4.3 | Maximum vibration limit : | grade A - IEC 60034-14:2018 Table 1 |  | grade A - IEC 60034-14:2018 Table 1 | [5 empty] | select | grade A - IEC 60034-14:2018 Table 1 | grade B - IEC 60034-14:2018 Table 1 | other
91 |  | Sensor type for vibration measurement : | not required |  | not required | [5 empty] | select | one stainless steel shock pulse monitoring nipple per bearing | one accelerometer per bearing | other | not required
92 |  | Noise
93 | 11.3.2.1,Table 22 | Sound pressure level at no load : | IEC 60034-9 limits | dB(A) | IEC 60034-9 limits | dB(A) |  |  |  |  | select | IEC 60034-9 limits | other
94 |  | Anti-condensation heaters
95 | 11.4.9.1,11.4.9.2 | Anti-condensation heater : | not required |  | not required | [5 empty] | select | windings | windings and line conductor terminal box | not required
96 | 11.4.9.2 | Anti-condensation heater supply voltage (AC) : | not applicable | V | not applicable | V |  |  |  |  | select | 100-120 single phase | 200-240 single phase | not applicable
97 | 11.4.9.2,11.4.9.3 | Separate anti-condensation heater terminal box : | not applicable |  | not applicable | [5 empty] | select | required | not required | not applicable
98 | 11.4.9.3 | Warning label language : | not applicable |  | not applicable | [5 empty] | select | English | other | not applicable
99 |  | Temperature monitoring
100 | 11.4.8.1,8.6.1 | Winding temperature detection : | select |  | select | [5 empty] | select | one thermistor (PTC) per phase | two thermistors (PTCs) per phase
101 |  | Terminal boxes
102 |  | Terminal box ingress protection : | select |  | select | [5 empty] | select | IP55 | IP56 | other
103 | 11.4.5.2 | Line conductor terminal box location viewed from drive end : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | top | right | left | bottom
104 |  | Line conductor cable quantity per phase : | input data |  | input data
105 |  | Line conductor cable type : | input data |  | input data
106 |  | Line conductor size : | select | mm² | select | mm² |  |  |  |  | select | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | other
107 | 11.4.5.3 | Line conductor terminal box cable gland entries : | input data |  | input data
108 |  | Line conductor terminal box size : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | one size above standard | two size above standard
109 |  | Miscellaneous
110 |  | Provision for IoT hardware installation : | not required |  | not required | [5 empty] | select | required | not required
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Specify the unique tag number for the equipment.
Note on C5: Specify the functional description of the equipment.
Note on C7: Select the CAS level to be applied in IOGP S-703Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C8: Specify the country in which the project is located, in accordance with ISO 3166-1.
Note on C9: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C10: Select the location of the facility where the equipment will be permanently installed.
Note on C11: Select the status of the order.
Note on C12: Specify the name of the motor manufacturer.
Note on C13: Specify the model number of the motor.
Note on C14: Select the required number of poles. If "other" is selected, specify the pole requirements in "Additional notes".
Note on C15: Specify the motor frame size/designation. Where this is not specified by the purchaser, supplier to specify the frame size as per the standard offering for the application.
Note on C16: Specify the manufacturer of the converter from which the motor is to be driven.
Note on C17: Specify the model number of converter from which the motor is to be driven.
Note on C19: Select the location where the motor is to be situated. If "other" is selected, specify in "Additional notes".
Note on C20: This is the altitude above sea-level. The IEC 60034-1 default is 1 000 m. If "other" is selected, specify the value in "Additional notes" only if the site conditions are higher than 1 000 m. Default value : 1 000 or below
Note on C21: The IEC 60034-1 default is 40 °C. Select a value different from 40 °C only if the site conditions are higher than the IEC default. "If other" is selected, specify the temperature values in "Additional notes". Default value : 40
Note on C22: Select "other" and specify the value in "Additional notes" only if the site conditions are lower than 0 °C . Default value : 0
Note on C23: Specify the chemicals or corrosives that may be present in the location environment (e.g. presence of H2S).
Note on C24: Select "yes" for unusual service conditions not covered elsewhere in IOGP S-704 such as salt-laden and abrasive dust . Specify unusual service conditions in "Additional notes". Default value : no
Note on C26: Select the hazardous area zone classification in which the motor is installed.
Note on C27: Select which certification is acceptable for motors to be located in a hazardous area. If "other" is selected, specify the certification in "Additional notes".
Note on C28: Select the temperature class for which the motor is rated for in accordance with IEC 60079.
Note on C29: Select the gas/dust group for which the motor is to be rated in accordance with IEC 60079.
Note on C30: Select the equipment protection level (EPL) in accordance with IEC 60079-14.
Note on C31: Select the type of protection for which the motor is rated for in accordance with IEC 60079.
Note on C33: Select the duty type as defined in IEC-60034-1, Clause 4. The JIP33 default is S1. For converter-fed motors, duty S9 or S10 may be applicable depending on the load profile.
Note on C34: Select the direction of motor shaft rotation observed while facing the drive end when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C35: Select the equipment intended to be driven by the high-voltage motor. If "other" is selected, specify details of the driven equipment in "Additional notes".
Note on C36: Select the method of power transfer to the driven equipment. Specify the load drive with details in "Additional notes". Include the gearbox data sheet when provided.
Note on C37: Purchaser to specify the maximum external radial loading where applicable. Supplier to specify the maximum permissible radial loading if not specified by the purchaser.
Note on C38: Purchaser to specify the maximum external axial loading on the shaft end where applicable. Supplier to specify the maximum permissible axial loading if not specified by the purchaser.
Note on C39: Specify the moment of inertia (MR²) of the load at the motor shaft.
Note on C41: Specify the input voltage, expressed in V, for which the motor is rated.
Note on C42: Select the supply frequency for which the motor is rated.
Note on C44: Select the insulation class of motor in accordance with IEC 60085. Default value : F
Note on C45: Select the temperature rise class of motor in accordance with IEC 60085. Specify another temperature rise value in the "Additional notes" column to offset the effect of extended stopping time. Default value : B
Note on C47: Select the load condition as seen by the motor at starting taken from the driven equipment data sheet. Specify the load information in "Additional notes" (e.g. valve open/close, damper open/close) and provide the load curve of the driven equipment.
Note on C48: Specify the rotor moment of inertia (MR²) as defined in 3.24.
Note on C50: Select the converter operation mode based on the driven equipment type. Select "other" for a different or combination of torque and power characteristics and specify in "Additional notes".
Note on C51: Supplier to specify the rated output, i.e. the required motor shaft rated mechanical power, if not specified by the purchaser.
Note on C52: Specify the motor rated current while operating at the rated voltage and rated frequency.
Note on C53: Specify the steady-state asynchronous rotor speed while delivering the rated output at rated voltage and rated frequency.
Note on C54: Specify the maximum continuous motor operating speed required by the driven equipment.
Note on C55: Specify the minimum continuous motor operating speed required by the driven equipment.
Note on C56: Specify the steady-state asynchronous rotor torque while delivering the rated output at rated voltage and rated frequency.
Note on C57: Specify the maximum steady-state asynchronous torque that the motor develops when the motor is supplied at rated voltage and rated frequency, expressed as per the unit value of the rated (full load) torque.
Note on C58: Select the efficiency category (IE) in accordance with IEC 60034-30-2. Default value : IE2
Note on C59: Specify the efficiency of the motor while operating at rated output.
Note on C60: Specify the efficiency at the maximum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C61: Specify the efficiency at the minimum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C62: Specify the efficiency at the maximum continuous operating speed at the maximum torque value.
Note on C63: Specify the cosine of the angle between active power and apparent power when the motor is operated at rated output.
Note on C64: Specify the cosine of the angle between active power and apparent power at the maximum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C65: Specify the cosine of the angle between active power and apparent power at the minimum continuous operating speed at the upper torque value of the load window as per IEC 61800-2.
Note on C67: Select the surface corrosivity category in accordance with ISO 12944-2, 5.1.1. Default value : C3
Note on C68: Select the surface durability category in accordance with ISO 12944-1, 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme. Default value : medium (M) 7 to 15 years
Note on C69: Where the manufacturer's standard paint colour is unacceptable and "other" is selected, specify the paint colour requirements in "Additional notes". Default value : manufacturer's standard
Note on C71: Select the ingress protection value in accordance with IEC 60034-5. If "other" is selected, specify the motor enclosure ingress protection value in "Additional notes". Default value : IP55
Note on C72: Select the motor cooling method in accordance with IEC 60034-6. If "other" is selected, specify the motor cooling method in "Additional notes". Default value : IC4A1A1
Note on C73: Specify the fully assembled weight of the motor.
Note on C74: Select the motor mounting arrangement in accordance with IEC 60034-7.
Note on C75: Select whether jacking bolts for safe and standard means of alignment of the motor with the coupled equipment during installation are required. Default value : not required
Note on C76: Select whether a separate terminal box for monitoring device is required. Each monitoring device type will have a separate terminal block within the auxiliary terminal box. Default value : not required
Note on C77: Select the direction of rotation of fan observed while facing the drive end when connecting motor terminals U-V-W to supply L1-L2-L3. Default value : bidirectional
Note on C78: Select the material for the external fan impeller. Default value : manufacturer's standard
Note on C79: Select the hardware material for external screws, bolts, nuts, washers and any other fixings. If "other" is selected, specify the details of hardware material used for the motor enclosure in "Additional notes". Default value : manufacturer's standard
Note on C81: Select whether bearing insulation in motor is required. When both bearings are insulated, a suitable shaft grounding system may be provided on the rotor shaft. Default value : not required
Note on C82: Specify the drive end bearing type, model number and associated details.
Note on C83: Specify the non-drive end bearing type, model number and associated details.
Note on C84: Specify the required internal clearance of the bearing in accordance with ISO 5753-1. Default value : C3
Note on C85: Specify the approved (refer to 11.4.7.8) lubrication specification and associated product reference code for lubrication of re-greasable bearings.
Note on C86: Specify the up and down thrust loads for selection of appropriate bearings for motor in vertical orientation.
Note on C88: Select whether the vibration test procedure should follow the rigid mounting method similar to that of the mounting method at installation location or adopt the manufacturer's standard method of mounting while performing the test. Default value : manufacturer's standard
Note on C89: Select the required balancing grade to determine the permissible limits for residual unbalance to achieve the vibrations grade (maximum vibration limits). Default value : G 2,5
Note on C90: Select the maximum vibration limits in accordance with IEC 60034-14:2018, Table 1. If "other" is selected, specify the shaft displacement vibration limits in "Additional notes". Default value : grade A - IEC 60034-14:2018 Table 1
Note on C91: Select the sensor type for vibration measurement. Default value : not required
Note on C93: Select the maximum permissible motor A-weighted sound pressure level at a reference distance of 1 m at no load and rated speed. If “other”, specify value in “Additional notes”. For limits, refer to IEC 60034-9: 2021, Table 2 (50 Hz) or Table 3 (60 Hz). Default value : IEC 60034-9 limits
Note on C95: Select whether anti-condensation heaters in the motor are required. Default value : not required
Note on C96: Select the supply voltage for which the anti-condensation heater will be rated. Refer to the project specified voltage level applicable in the voltage range selected. Default value : not applicable
Note on C97: Select whether a separate anti-condensation heaters terminal box for the motor are required. Default value : not applicable
Note on C98: Select the language to be used for the label warning that heater terminals may be live when the motor is isolated. When the language is other than English, specify it in "Additional notes". Default value : not applicable
Note on C100: Select the winding temperature detection as required.
Note on C102: Select the ingress protection value in accordance with IEC 60034-5 for which the terminal boxes are rated.
Note on C103: Select the line conductor terminal box location when viewed from the drive end of the motor, using coding in accordance with IEC 60034-7:2020. For double ended motors, specify the requirement in "Additional notes". Default value : manufacturer's standard
Note on C104: Specify the number of runs of cable per phase.
Note on C105: Specify the line conductor cable type (e.g. single-core, multi-core, armoured, un-armoured).
Note on C106: Select the size (cross-section area) of the line conductor. Where the line conductor size is not yet determined, supplier to specify maximum size of cable acceptable into the supplied terminal box.
Note on C107: Select the number and size of cable gland entries in line terminal box (e.g. 1 x M32, 2 x M20). Where gland entry number and sizes are not yet determined, supplier to specify the terminal box cable gland entry details.
Note on C108: Select a larger than standard main terminal box as required where a higher size/rated power supply cable is anticipated. Where inappropriate for the specified cable details, supplier to select an appropriate terminal box size. Default value : manufacturer's standard
Note on C110: Select whether mounting provisions of IoT hardware provisions on the motor is required. Specify the mounting points and installation provisions in "Additional notes". IoT hardware may be procured and mounted by the purchaser at a later date. Default value: not required

## Supplement
Row |  | IOGP S-703D (1.1) Procurement Data Sheet for Low-voltage Three-phase Cage Induction Motors (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
IOGP S-703D (1.1) Procurement Data Sheet for
Low-voltage Three-phase Cage Induction Motors (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-703 Supplementary Specification to IEC 60034-1 for Low-voltage Three-phase Cage Induction Motors.
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft