## Front & preliminaries
|  |  | SPECIFICATION | August 2024
|  |  | IOGP S-703L | Version 1.1
Information Requirements for Low-voltage Three-phase Cage Induction Motors (IEC)
Revision history
VERSION | DATE | PURPOSE
1.1 | August 2024 | Issued for Public Review
1 | March 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-703L (1.1) Information Requirements for Low-voltage Three-phase Cage Induction Motors (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-703L (1.1) Information Requirements for Low-voltage Three-phase Cage Induction Motors (IEC)
Introduction
The purpose of this information requirements specification (IRS) is to specify information requirements for the procurement of low-voltage three-phase cage induction motors in accordance with IOGP S-703 for application in the petroleum and natural gas industries.
The IRS defines the information requirements, including format, timing and purpose, to be provided by the supplier. It also defines the specific conditions to be satisfied for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
The IOGP S-703 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), a procurement data sheet (PDS), this IRS and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Information Requirements Specification (IRS)
This IRS is to be applied in conjunction with the specification, the PDS and the QRS, referred to in this document as IOGP S-703, IOGP S-703D and IOGP S-703Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Instructions
IOGP S-703L (1.1) Information Requirements for Low-voltage Three-phase Cage Induction Motors (IEC)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS structure contents
| 1 | 'Front & preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes/No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information submission abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS.
Column K — 'Translation Required' (Yes/No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PDS |  | procurement data sheet
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| TRS |  | technical requirements specification
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3. Metadata listed below is as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The unique identifier for the 'document' according to the 'owner/operator' document numbering scheme. |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document. |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised. |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision. |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision. |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision. |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision. |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type. |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification code |  |  | A code that uniquely identifies an export control classification. |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
Table 3 — Supplier deliverable metadata
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
IOGP S-703L (1.1) Information Requirements for Low-voltage Three-phase Cage Induction Motors (IEC)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement.
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Document Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S703-IR-1 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | - | - |  | -
S703-IR-45 | Delivery schedule |  | Delivery/production schedule | Yes | For Information |  | - | - |  | -
S703-IR-46 | Progress report |  | Progress report | No | For Information |  | - | - |  | -
S703-IR-4 | Quality plan | Required for CAS A, CAS B | Quality plan | - | - |  | - | - |  | -
S703-IR-6 | Inspection and test plan |  | Inspection and test plan (ITP) | No | For Acceptance |  | - | - |  | -
S703-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
S703-IR-8 | Non-conformance records |  | Non-conformance records | No | For Acceptance |  | - | - |  | -
S703-IR-9 | Concession requests |  | Concession request | No | For Acceptance |  | - | - |  | -
Technical Information Deliverables
S703-IR-44 | Equipment data sheet |  | Manufacturer data sheet | No | For Acceptance |  | - | - |  | -
S703-IR-19 | General arrangement drawing |  | General arrangement diagram | Yes | For Acceptance |  | - | - |  | - | Preliminary information with proposal
S703-IR-47 | Single-speed motor performance curves |  | Motor performance and electrical data and curves | No | For Acceptance |  | - | - |  | -
S703-IR-40 | Converter duty motor performance curves | Where purchaser confirms the motor is converter-fed | Motor performance and electrical data and curves | No | For Acceptance |  | - | - |  | -
S703-IR-22 | Termination diagram | Where purchaser cable terminations are required in addition to that of the line conductors | Termination diagram | No | For Acceptance |  | - | - |  | -
S703-IR-48 | Lubrication data | To be provided for motors with re-greasable bearings and re-greasing ports | Lubrication list | No | For Information |  | - | - |  | -
S703-IR-49 | Installation manual |  | Installation manual | No | For Information |  | - | - |  | - | Installation manual index, if required, should be provided in first revision of the document. When index agreed, installation manual content shall be provided in subsequent revision of the document.
S703-IR-50 | Maintenance manual |  | Maintenance manual | No | For Information |  | - | - |  | - | Maintenance manual index, if required, should be provided in first revision of the document. When index agreed, maintenance manual content shall be provided in subsequent revision of the document.
S703-IR-35 | Operating manual |  | Operating manual | No | For Information |  | - | - |  | - | Operating manual index, if required, should be provided in first revision of the document. When index agreed, operating manual content shall be provided in subsequent revision of the document.
S703-IR-51 | Factory acceptance test (FAT) protocol | Required only where tests in addition to those stated in IEC 60034-1,Table 16 have been specified by the purchaser in the purchase order | Factory acceptance test (FAT) procedure | Yes | For Acceptance |  | - | - |  | -
S703-IR-52 | Factory acceptance test (FAT) records | Required for CAS A, B and C | Factory acceptance test (FAT) records | - | - |  | - | - |  | -
S703-IR-29 | Type test certificate | Required for CAS A, B and as per IOGP S-703-Q | Type test report | - | - |  | - | - |  | -
S703-IR-26 | Hazardous area certificate (type) | Motor rated for use in hazardous area | Hazardous area certificate | No | For Information |  | - | - |  | -
S703-IR-39 | Vibration test report | Where the purchaser selects vibration test with rigid mounting in the data sheet | Vibration level test report | No | For Acceptance |  | - | - |  | -
S703-IR-30 | Declaration of conformity |  | Declaration of conformity | No | For Information |  | - | - |  | -
S703-IR-53 | Manufacturer record book (MRB) |  | Manufacturer record book (MRB) | No | For Information |  | - | - |  | - | Manufacturer record book index, if required, shall be provided in first revision of the document. When index agreed, manufacturer record book content shall be provided in subsequent revision of the document.
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
IOGP S-703L (1.1) Information Requirements for Low-voltage Three-phase Cage Induction Motors (IEC)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S703-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S703-IR-45 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S703-IR-46 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities.. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S703-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF | CFIHOS-70000451
S703-IR-6 | Inspection and test plan | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. |  | PDF | CFIHOS-70000180
S703-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and requirements, d. preservation requirements detailing inspection periods and required maintenance, materials including lubricants required etc., both prior to installation and post installation, but prior to commissioning. | 6.6 | PDF | CFIHOS-70000154
S703-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S703-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000389
Technical Information Deliverables
S703-IR-44 | Equipment data sheet | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data containing part number/model, design information, operational data and limitations of the equipment. The equipment data sheet shall include all relevant design data and information required for power system study, including but not limited to, - motor data (basic design, hazardous area classification, enclosure, mounting, bearing, heaters and auxiliaries, monitoring sensors & detectors, terminals and terminal boxes, etc.) - performance data (starting, operating, etc.) | 11.3.1.3, 11.3.2.1, 11.4.10.1, 11.4.3.1, 11.4.7.1, 11.4.7.2, 11.4.7.4, 11.4.7.5, 11.4.7.7, 11.4.7.9, 5.9.1, 5.9.2, 6.1, 6.8.1, 7.4, 8.6.1, Table 22, Table 23, Table 24, Table 25 | PDF | CFIHOS-70000416
S703-IR-19 | General arrangement drawing | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards. For equipment / components the drawing may include cross sectional views. The drawing shall include cross sectional views if a separate document for detailed drawing is not furnished. The drawing shall contain the following minimum information- - Main dimensions – overall, withdrawal/installation and maintenance clearances. - Drawings – dimensional outline, cross sections, details of parts (shaft end details, terminal box, bearings, etc.). - Interface connections (including earthing points where applicable). - Weight - Centre of gravity - Location, orientation, and dimensions of all terminal boxes. - Installation and mounting details - Lifting arrangement - Drawings - motor information (ratings, lubrication data, labels & markings, etc.) in accordance with IEC 60034-1:2022, clause 10 and IOGP S-703. | 10.4.6, 10.3, 10.4.2, 11.1, 11.4.11.2, 11.4.2.1.1, 11.4.2.1.2, 11.4.2.2.1, 11.4.2.2.2, 11.4.2.2.3, 11.4.2.3.1, 11.4.2.3.2, 11.4.2.3.3, 11.4.4.4, 11.4.5.2, 11.4.5.3, 11.4.6.1, 11.4.7.3, 11.4.9.2, 11.4.9.3, 6.8.1, Table 23 | PDF | CFIHOS-70000153
S703-IR-47 | Single-speed motor performance curves | Curves to indicate torque and current against speed for 80% and 100% voltage conditions and at rated frequency, superimposed on driven equipment torque curve to confirm that there is adequate net torque for acceleration. Motor performance curves shall include the following information: - Torque curve at 80% rated voltage expressed as a percentage of rated torque. - Torque curve at rated voltage expressed as a percentage of rated torque. - Power factor curve at rated voltage. - Current curve at 80% rated voltage expressed as a percentage of rated current. - Current curve at rated voltage expressed as a percentage of rated current. - Torque curve of the load expressed as a percentage of rated torque. | Table 22 | PDF | 70000449
S703-IR-40 | Converter duty motor performance curves | Performance data/curve to include the following: Data for continuous operating region of converter as per IEC 61800-2:2021, 5.3.3.2 and Figure 10. - rated torque (MN) [N⋅m]; - rated speed (NN) [r/min]; - maximum rated speed (NNMax) [r/min]; - minimum rated speed (NNMin) [r/min]; - minimum speed (NMin) [r/min]; - maximum rated safe speed (NSNMax) [r/min]; - rated output power (PsN) [kW]. Voltage/frequency characteristics as per IEC TS 60034-25:2022, Figure 3, indicating maximum converter output voltage, field-weakening frequency and maximum allowable frequency. Converter duty motor operating data as per below: - voltage (V) - current (A) - power factor (pu) - efficiency (%) - torque (Nm) - speed (min-1) - frequency (Hz) for the following operating conditions: maximum torque at minimum rated speed (NNMin) maximum torque at rated speed (NN ) maximum torque at maximum rated speed (NNMax) | Table 22 | PDF | CFIHOS-70000449
S703-IR-22 | Termination diagram | A diagram which identifies all connections and cable terminations to facilitate installation, removal, maintenance and fault finding. To include - - Vendor interfaces; - Motor terminations; - Instrument and auxiliary terminations; - Package interfaces (Control panels, relay panels, converters, switchboards, electrical network system, etc.) terminations. | 10.4.2 | PDF | CFIHOS-70000330
S703-IR-48 | Lubrication data | Schedule to indicate type and grade of lubricants and other consumables required for all equipment supplied. For each schedule entry the following is also to be included as a minimum: Tag number, tag description / component (e.g. bearings, etc.), lubricant manufacturer, lubricant type and grade (product reference code and specification) and frequency of change. For re-greasable rolling element bearings: - Re-greasing amounts per bearing - Re-greasing intervals according to running speeds and ambient temperatures - Re-greasing procedure | 11.4.7.6, 11.4.7.8, Table 26 | PDF | CFIHOS-70000444
S703-IR-49 | Installation manual | The manual shall provide information regarding normal and safe methods of handling, installation of motor and auxiliaries. Installation refers to the mounting, setting, erection, etc. NOTE Unless otherwise agreed, can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a standalone document. | 11.4.7.6, Table 26 | PDF | CFIHOS-70000181
S703-IR-50 | Maintenance manual | The manual shall provide information of manufacturer's recommended methods and practices for inspection and maintenance of motor and auxiliaries. This shall be complete with information for both hardware and software regarding predictive/preventive maintenance, fault detection/diagnosis and fault isolation/rectification and ensuring equipment reliability. The instructions shall include information concerning: - the nature and frequency of inspections; - safety precautions and warnings for maintenance carried out on running or live equipment; - information for fault diagnosis and identification; - instructions for repairs and adjustments; - description of built-in diagnostic systems to aid fault finding, when applicable; - information on need for and use of special tools and tackles, where applicable; - drawings and diagrams enabling maintenance personnel to carry out their task rationally (especially fault-finding tasks); - regular checking of warning devices; - description of all predictable tasks performed at specific intervals to be consolidated in the form of maintenance schedules and, if necessary, master schedules; Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a standalone document. | 11.4.7.6, Table 26 | PDF | CFIHOS-70000206
S703-IR-35 | Operating manual | The manual shall provide information of methods and modes of operating motor and auxiliaries, including but not limited to instructions, procedures, drawings, tables, etc. for the operation (stop, start), control and emergency shutdown. This shall be complete with information regarding operational limits, control functions, testing interlocks and safeties, possible interruptions, corrective actions, hazards and corrective measures to be taken. NOTE Unless otherwise agreed, can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a standalone document. | 11.4.7.6, Table 26 | PDF | CFIHOS-70000228
S703-IR-51 | Factory acceptance test (FAT) protocol | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements,. to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. REFER TO CONDITION INVOKING REQUIREMENT | 11.4.4.1, 11.4.4.2, 11.4.4.3, Table 16, Table 22 | PDF | CFIHOS-70000427
S703-IR-52 | Factory acceptance test (FAT) records | The FAT report will be used to verify that the equipment has been tested according to FAT protocol. The FAT report will be used for acceptance of the equipment delivery. This document shall include all results from the activities performed in routine tests, additional tests (if any) requested by purchaser, FAT protocol, applicable standards, specifications and requirements. Every test report/result in addition to the inspection/measurements/data/graphs/charts/prints, should be endorsed with the following information as a minimum - Date of testing; - Signature of person responsible for test; - Object identification (type, series number, etc.); - Statement of compliance, where applicable; - Test set-up and equipment / instruments used; - Reference to test procedure; - A list of punch items on the observations during the FAT that require corrective action (modification/replacement/repair) for acceptance shall be included in this document. | 11.4.4.1, 11.4.4.2, 11.4.4.3, Table 16, Table 22 | PDF | CFIHOS-70000429
S703-IR-29 | Type test certificate | The certificate to confirm that the results of test performed to provide evidence that the design meets the requirements of the functional specification (See ISO 13880:1999). (When specified, type test shall be independently verified by a third party and supported by a Certificate of Conformance - CFIHOS-70000013). | 11.3.1.1, 11.3.1.2, 11.4.11.1.2, 11.4.4.5, Table 22 | PDF | CFIHOS-70000245
S703-IR-26 | Hazardous area certificate (type) | Attestations issued by a recognized independent authority certifying that the motor and all its auxiliary components have satisfied the requirements for use in hazardous area. | ****, 11.4.11.1.1, 11.4.11.1.2, 11.4.11.2, 11.4.6.2 | PDF | CFIHOS-70000160
S703-IR-39 | Vibration test report | Vibration level test report stating maximum vibration levels of machine as defined in IEC 60034-14 | 11.4.4.2 | PDF
S703-IR-30 | Declaration of conformity | Declaration that contains sufficient information to enable a recipient of the declaration of conformity to identify the issuer of the declaration, the object of the declaration, the standards and other specified requirements with which conformity is declared, and the person signing for and on behalf of the issuer of the declaration of conformity (first party). Declares conformance with all standards relating to the motor in its region of use, and its duty as defined by the purchaser in the procurement specification. | 11.4.1.1, 11.4.1.2 | PDF | CFIHOS-70000431
S703-IR-53 | Manufacturer record book (MRB) | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and supplier. The document shall include, but not be limited to, the following: - calculations and study reports - documents recording compliance with statutory and/or local regulations, and inspection and testing results - documents recording compliance with environmental requirements for installed components - reports for all the testing carried out at supplier / sub-supplier shop, e.g. Noise report, Vibration report, Any other test report or measurement data that is not part of Factory acceptance test (FAT) records. - documents related to sub-supplier certificates, test reports and catalogues, - documents related to declaration of conformity. - any other information about the motor, its associated system or components, etc. that would be required for installation, testing, commissioning, operation and maintenance. | Table 22 | PDF | CFIHOS-70000178
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Back cover
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: