## Front & Preliminaries
|  |  |  | SPECIFICATION | January 2025
|  |  |  | IOGP S-753D | Version 0.1
Procurement Data Sheet for
Battery Energy Storage Systems (BESS) (IEC)
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | January 2025 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-753D (0.1) Procurement Data Sheet for
Battery Energy Storage Systems (BESS) (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-753D (0.1) Procurement Data Sheet for
Battery Energy Storage Systems (BESS) (IEC)
Introduction
The purpose of this procurement data sheet is to define purchaser specific requirements for the procurement of battery energy storage systems (BESSs) in accordance with IOGP S-753 for application in the petroleum and natural gas industries. The procurement data sheet provides project specific requirements where the specification requires the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents can be listed in the procurement data sheet to define scope and technical requirements for enquiry and purchase of the equipment.
This procurement data sheet shall be used in conjunction with the specification (IOGP S-753), information requirements specification (IOGP S-753L) and quality requirements specification (IOGP S-753Q) which together comprise the full set of specification documents. The introduction section in the specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Procurement Data Sheet
Row | IOGP S-753D (0.1) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC) | [6 empty] | Issue
2 | Ref. Clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General
4 |  | BESS tag number : | input data |  | input data
5 |  | BESS tag description : | input data |  | input data
6 | 4.1,7.5 | Purchase order reference and date : | input data |  | input data
7 | 7.5 | BESS supplier : | input data |  | input data
8 |  | Project requirements
9 | 5.2.3.1 | Project country : | input data |  | input data
10 | 5.2.4.1,8.3.1.1,8.3.2.6,9.1.1,9.2.1 | Project region : | input data |  | input data
11 | 5.3.1,5.3.2,5.4.1,Figure 4 | Service life : | 10 | years | 10 | years |  |  |  |  | Select | 10 | 15 | other
12 | 4.2.4,5.2.2.2,5.5.1.4,8.3.1.1,8.3.2.6,9.1.1,9.2.1 | Local codes or regulatory standards : | input data |  | input data
13 | 4.2.4,5.2.2.1,5.2.2.3,5.5.1.4,5.5.3 | Grid codes : | input data |  | input data
14 | 5.8.1,5.8.2 | Certification marine/offshore : | not required |  | not required | [5 empty] | Select | not required | DNV | Lloyds | ABS | USCG | NRTL | other
15 |  | Paint colour : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
16 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | Select | A | B | C | D
17 |  | Installation
18 | 5.2.1,5.2.3.3,5.8.1,5.8.2,9.2.2,9.2.5 | Site : | select |  | select | [5 empty] | Select | onshore | offshore - fixed | offshore - floating | marine (ship) | other
19 | 5.2.1,5.2.3.3,9.2.1,9.2.2,9.2.5 | Location of installation : | outdoor |  | outdoor | [5 empty] | Select | indoor | outdoor | other
20 |  | Environmental conditions - design and operation
21 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Minimum ambient temperature : | ≥ −10 | °C | ≥ −10 | °C |  |  |  |  | Select | ≥ −10 | ≥ −25 | ≥ −40 | other
22 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Maximum ambient temperature : | ≤ 40 | °C | ≤ 40 | °C |  |  |  |  | Select | ≤ 40 | other
23 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Average ambient temperature : | ≤ 35 | °C | ≤ 35 | °C |  |  |  |  | Select | ≤ 35 | other
24 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Design ambient temperature : | ≤ 40 | °C | ≤ 40 | °C |  |  |  |  | Select | ≤ 40 | other
25 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Solar radiation intensity : | select | W/m2 | select | W/m2 |  |  |  |  | Select | negligible | ≤ 500 (low) | < 500 to ≤ 700 (medium) | < 700 to ≤ 1120 (high) | other
26 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Maximum altitude : | ≤ 1 000 | m | ≤ 1 000 | m |  |  |  |  | Select | ≤ 1 000 | other
27 | 5.1,5.2.1,5.2.3.3,8.3.1.8,8.4.8,9.2.2,9.2.5 | Non-condensing relative humidity - 24 h average : | ≤ 95 | % | ≤ 95 | % |  |  |  |  | Select | ≤ 95 | other
28 | 5.1,5.2.1,5.2.3.3,9.2.5 | Condensation and precipitation : | no |  | no | [5 empty] | Select | yes | no
29 | 5.1,5.2.1,5.2.3.3,5.2.3.4,5.2.3.5,5.2.3.6,5.4.1,5.8.2,8.4.8,9.2.2,9.2.5,B.3 | Special environmental conditions : | input data |  | input data
30 | 12.4,12.5,5.2.3.4,5.2.3.5,5.2.3.6,9.2.5 | Environmental contamination : | none |  | none | [5 empty] | Select | none | salt-laden | H2S | salt-laden and H2S | other
31 | 5.1,5.2.1,5.2.3.2 | Seismic activity zone in accordance with IEC 60721-2-6 : | select |  | select | [5 empty] | Select | Zone 1 | Zone 2 | Zone 3 | Zone 4 | not applicable | other
32 | 5.8.1,5.8.2 | Maximum rolling of vessel in dynamic conditions : | input data |  | input data
33 | 5.8.1,5.8.2 | Maximum pitching of vessel in dynamic conditions : | input data |  | input data
34 |  | Environmental conditions - transportation and storage
35 | 12.1,12.2,12.3,12.4,12.5 | Minimum ambient temperature - transportation and storage : | ≥ −10 | °C | ≥ −10 | °C |  |  |  |  | Select | ≥ −10 | ≥ −25 | ≥ −40 | other
36 | 12.1,12.2,12.3,12.4,12.5 | Maximum ambient temperature - transportation and storage : | ≤ 40 | °C | ≤ 40 | °C |  |  |  |  | Select | ≤ 40 | other
37 | 12.1,12.2,12.3,12.4,12.5 | Maximum non-condensing relative humidity - transportation and storage : | ≤ 95 | % | ≤ 95 | % |  |  |  |  | Select | ≤ 95 | other
38 | 12.1,12.2,12.3,12.4,12.5 | Equipment preservation during transportation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
39 | 12.1,12.2,12.3,12.4,12.5 | Storage site : | select |  | select | [5 empty] | Select | indoor - climate controlled (humidity and temperature) | indoor - temperature controlled only | indoor - natural ventilation | outdoor | other
40 | 12.1,12.2,12.3,12.4,12.5 | Additional or unusual conditions - transportation and storage : | input data |  | input data
41 |  | Power system interface parameters
42 | 5.2.1,5.2.2.1 | Nominal voltage : | input data | kV | input data | kV
43 | 5.2.1,5.2.2.1 | Steady state voltage variation : | ±10 | kV | ±10 | kV |  |  |  |  | Select | ±10 | other
44 | 5.2.1,5.2.2.1 | Temporary voltage variation : | input data | select | input data | select |  |  |  |  | Select | % | min
45 | 5.2.1,5.2.2.1 | Nominal frequency : | 50 | Hz | 50 | Hz |  |  |  |  | Select | 50 | 60
46 | 5.2.1,5.2.2.1 | Steady state frequency variation : | ±1 | % | ±1 | % |  |  |  |  | Select | ±1 | ±3 | other
47 | 5.2.1,5.2.2.1 | Temporary frequency variation : | input data | select | input data | select |  |  |  |  | Select | % | min
48 | 5.2.1,5.2.2.1 | Minimum and maximum short circuit current : | input data | kA | input data | kA
49 | 5.2.1,5.2.2.1 | System earthing : | select |  | select | [5 empty] | Select | solidly earthed neutral | impedance earthed neutral | isolated neutral | other
50 | 5.2.2.3 | Individual harmonic distortion of voltage compatibility level : | Class 2 |  | Class 2 | [5 empty] | Select | Class 1 | Class 2 | Class 3
51 | 5.2.2.3 | Total harmonic distortion of voltage compatibility level : | Class 2 |  | Class 2 | [5 empty] | Select | Class 1 | Class 2 | Class 3
52 |  | Auxiliary power supply parameters
53 | 5.4.4 | Nominal voltage : | input data | V | input data | V
54 | Figure 1 c | Source of auxiliary power supply : | externally fed |  | externally fed | [5 empty] | Select | internally fed | externally fed
55 | 5.4.4 | Steady-state voltage variation : | ±10 | % | ±10 | % |  |  |  |  | Select | ±10 | other
56 | 5.4.4 | Nominal frequency : | 50 | Hz | 50 | Hz |  |  |  |  | Select | 50 | 60
57 | 5.4.4 | Steady state frequency variation : | ±1 | % | ±1 | % |  |  |  |  | Select | ±1 | ±3 | other
58 | 5.4.4 | Minimum and maximum short circuit current : | input data | kA | input data | kA
59 | 5.4.4 | System earthing : | select |  | select | [5 empty] | Select | solidly earthed neutral | impedance earthed neutral | isolated neutral | other
60 | 5.4.4 | Maximum auxiliary power consumption : | input data | kW | input data | kW
61 |  | BESS safety
62 | 7.2 | Additional language for safety labels and markings : | input data |  | input data
63 | 7.7 | Maximum acoustic noise level at a distance of 1 m : | manufacturer's standard | dBA | manufacturer's standard | dBA |  |  |  |  | Select | manufacturer's standard | other
64 |  | Hazard identification and risk analysis documentation : | not required |  | not required | [5 empty] | Select | not required | required
65 |  | System risk reduction measures documentation : | not required |  | not required | [5 empty] | Select | not required | required
66 |  | BESS design data
67 | 8.1,Table 9 | BESS category : | select |  | select | [5 empty] | Select | V-H | E-L | S-U | C-A | other
68 | 5.1,5.2.1,5.4.1,5.5.1.2 | BESS application : | select |  | select | [5 empty] | Select | Class A - frequency regulation | Class A - reduction of power fluctuation | Class A - voltage regulation | Class B - peak shaving / peak shifting | Class C - back-up power
69 | 4.2.4,5.5.2,5.5.3,5.5.4 | Operation states required : | input data |  | input data
70 | 5.1,5.3.1,5.4.2 | Rated active input power : | input data | select | input data | select |  |  |  |  | Select | kW | MW
71 | 5.1,5.3.1,5.4.2 | Rated reactive input power : | input data | select | input data | select |  |  |  |  | Select | kVAR | MVAR
72 | 5.1,5.3.1,5.4.2 | Rated active output power : | input data | select | input data | select |  |  |  |  | Select | kW | MW
73 | 5.1,5.3.1,5.4.2 | Rated reactive output power : | input data | select | input data | select |  |  |  |  | Select | kVAR | MVAR
74 | 5.1,5.3.1,5.4.2 | Rated energy storage capacity at beginning of life : | input data | select | input data | select |  |  |  |  | Select | kWh | MWh
75 | 5.5.1.2 | BESS functional description : | input data |  | input data
76 |  | BESS duty cycle
77 | 5.1,5.3.1 | BESS duty cycle profile and description : | input data |  | input data
78 |  | Accumulation subsystem (secondary batteries)
79 | 8.1,Table 9 | Battery chemistry : | lithium iron phosphate - LFP (LiFePO4) |  | lithium iron phosphate - LFP (LiFePO4) | [5 empty] | Select | lithium iron phosphate - LFP (LiFePO4) | lithium nickel manganese cobalt oxide - NMC (LiNiMnCoO2) | other
80 | 8.3.1.1,8.3.2.1,8.4.1 | Battery housing : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
81 | 8.3.1.1,8.3.1.2,8.3.1.7 | Fire resistance rating for battery housing : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | A0 | A60 | A120 | other
82 |  | Power conversion subsystem
83 | 8.3.1.1 | PCS housing : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
84 |  | Fire and gas system
85 | 9.1.5 | Fire suppression system for battery housing : | required |  | required | [5 empty] | Select | required | not required | other
86 | B.2 | Fire and gas audible alarm : | not required |  | not required | [5 empty] | Select | required | not required
87 |  | Communication interfaces
88 | 4.2.4,5.6.2,5.6.3.1,Table 3 | BESS message category for remote monitoring and control : | category II |  | category II | [5 empty] | Select | category I | category II | category III
89 | 4.2.4,5.6.3.1,5.6.3.3 | Interface media for ECMS/PMS : | Ethernet (fiber) |  | Ethernet (fiber) | [5 empty] | Select | not required | hardwired discrete | serial | Ethernet (Cu) | Ethernet (fiber) | wireless | other
90 | 4.2.4,5.6.3.1,5.6.3.3 | Interface protocol for ECMS/PMS : | Ethernet IP |  | Ethernet IP | [5 empty] | Select | not applicable | potential free contact | RS485 | Modbus TCP/IP | Profinet | Ethernet IP | other
91 | 4.2.4,5.6.3.1,5.6.3.3 | Interface network redundancy for ECMS/PMS : | not required |  | not required | [5 empty] | Select | not required | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other
92 | 4.2.4,5.6.3.1,5.6.3.3 | BESS remote access - via interface for ECMS/PMS : | yes - read only |  | yes - read only | [5 empty] | Select | no | yes - read only | yes - read/write
93 | 9.1.7 | Interface media for external FGS : | not required |  | not required | [5 empty] | Select | not required | hardwired discrete | Ethernet (fiber) | other
94 | 9.1.7 | Interface protocol for external FGS : | not applicable |  | not applicable | [5 empty] | Select | not applicable | potential free contact | Ethernet IP | other
95 | 4.2.4 | Interface media for external ESD system : | not required |  | not required | [5 empty] | Select | not required | hardwired discrete | other
96 | 4.2.4 | Interface protocol for external ESD system : | not applicable |  | not applicable | [5 empty] | Select | not applicable | potential free contact | other
97 | 4.2.4,5.6.3.1,5.6.3.3 | Hardware for remote access : | required |  | required | [5 empty] | Select | required | not required
98 |  | Interconnecting cables
99 | 5.7.3.1 | Interconnecting cables between BESS equipment or subsystems : | required |  | required | [5 empty] | Select | required | not required
100 | 5.7.3.1 | Cable type : | input data |  | input data
101 |  | Additional scope of supply
102 | 10.1 | Isolation or coupling transformer upstream of BESS (PCS) : | not required |  | not required | [5 empty] | Select | required | not required
103 | 10.2 | Distribution transformer for externally fed auxiliary power supply of BESS : | not required |  | not required | [5 empty] | Select | required | not required
104 | 11 | HV switchgear and associated devices upstream of BESS (PCS) : | not required |  | not required | [5 empty] | Select | required | not required
105 |  | Transport, storage and handling
106 | 12.1,12.2,12.3,12.4,12.5 | Transport, storage and handling : | manufacturer's standard |  | manufacturer's standard | [5 empty] | Select | manufacturer's standard | other
107 | 12.3 | Quantity of portable battery module lifting trolley required : | not required |  | not required | [5 empty] | Select | not required | 1 | 2 | other
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Specify the unique tag number of the BESS.
Note on C5: Specify the functional description of the BESS.
Note on C6: Specify the purchase order reference and date. If there is no data to specify, input "not applicable".
Note on C7: Specify the name of the supplier. If the supplier is a system integrator, also specify the names of the sub-suppliers for the PCS and battery, along with the name of the system integrator.
Note on C9: Specify the country where the project is located in accordance with ISO 3166-1. This information is necessary for the supplier to provide the appropriate product marking and certification for the region.
Note on C10: Specify the geographic location, within the country, which will determine the applicability of local regulatory requirements.
Note on C11: Select the required service life of the BESS in accordance with the project design basis, ensuring that the supplier can design the system accordingly. If "other" is selected, specify details in the "Additional notes" column. Default value : 10
Note on C12: Specify the relevant local codes, regulatory standards, greenhouse policies, or company-specific requirements. If there is a document that encompasses all codes or standards, specify the document number in the "Additional notes" column.
Note on C13: Specify the applicable grid codes that the BESS should adhere to. If there is a document that encompasses all codes or standards, specify the document number in the "Additional notes" column.
Note on C14: Select the required marine/offshore certification authority that the BESS should adhere to. Applicable for marine/offshore installations. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C15: Select the required option for the BESS equipment external paint colour. If "other" is selected, specify details of the required painting standard (e.g. RAL, MUNSSEL, ANSI) in the "Additional notes" column. Default value : manufacturer's standard
Note on C16: Select the CAS level to be applied in IOGP S-753Q, Annex A. CAS D requires the fewest quality interventions and information requirements. Default value : D
Note on C18: Select the location of the facility where the BESS will be permanently installed. If "other" is selected, specify details in the "Additional notes" column.
Note on C19: Select the permanent installation location for the BESS. If "other" is selected, specify details of the location such as under shelter, inside an outdoor building or within a room in the "Additional notes" column. Default value : outdoor
Note on C21: Select the expected minimum ambient temperature for the area surrounding the BESS . If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≥ −10
Note on C22: Select the expected maximum ambient temperature for the area surrounding the BESS . If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 40
Note on C23: Select the expected 24 h average ambient temperature for the area surrounding the BESS . If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 35
Note on C24: Select the required design ambient temperature for the area surrounding the BESS. If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 40
Note on C25: Select the expected solar radiation intensity. If "other" is selected, specify another intensity or a reference to an applicable document (e.g. procedure) in the "Additional notes" column.
Note on C26: Select the installation altitude above sea level. If "other" is selected, specify another altitude or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 1 000
Note on C27: Select the expected non-condensing relative humidity. If "other" is selected, specify another percentage or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 95
Note on C28: If "yes" is selected, specify the form of precipitation in the "Additional notes" column. Precipitation characteristics for insulation are detailed in IEC 60060-1 and 60071-1. For other properties, refer to IEC 60721-2-2. Default value : no
Note on C29: Specify any expected special environmental conditions (e.g. dust, corrosion, flood, or wind). If corrosive environment conditions are specified, specify the corrosion category in accordance with EN ISO 12944-2 in the "Additional notes" column.
Note on C30: Select the applicable contaminant exposure to the BESS. If "other" is selected, specify another type of contamination or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : none
Note on C31: Select the seismic activity zone as defined in IEC 60721-2-6 for the location where the equipment is to be used. Where seismic certification is not required, select "not applicable".
Note on C32: For floating or marine locations, specify the maximum rotation about fore-and-aft axis of the vessel under dynamic conditions defined in IEC 60092-101, e.g. ± 22° 30'. Specify "not applicable" where not applicable.
Note on C33: For floating or marine location, specify the maximum rotation about athwartship axis of the vessel under dynamic conditions defined in IEC 60092-101, e.g. ± 7° 30'. Specify "not applicable" where not applicable.
Note on C35: Select the expected minimum ambient temperature for transportation and storage. If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≥ −10
Note on C36: Select the expected maximum ambient temperature for transportation and storage. If "other" is selected, specify another temperature or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 40
Note on C37: Select the expected maximum non-condensing relative humidity for transportation and storage. If "other" is selected, specify another percentage or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : ≤ 95
Note on C38: Select the requirements for equipment preservation during transportation. If "other" is selected, specify another type of preservation or a reference to an applicable document (e.g. procedure) in the "Additional notes" column. Default value : manufacturer's standard
Note on C39: Select the appropriate storage location for the BESS. If "other" is selected, specify another site or a reference to an applicable document (e.g. procedure) in the "Additional notes" column.
Note on C40: Specify any additional or unusual conditions expected (e.g. long storage of batteries) during transportation and storage.
Note on C42: Specify the nominal voltage at the power system interface point.
Note on C43: Select the expected steady state voltage variation at the power system interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±10
Note on C44: Specify the expected temporary voltage variation and its duration at the power system interface point.
Note on C45: Select the nominal frequency at the power system interface point. Default value : 50
Note on C46: Select the expected steady state frequency variation at the power system interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±1
Note on C47: Specify the expected temporary frequency variation and its duration at the power system interface point.
Note on C48: Specify the value of minimum and maximum short circuit current at the power system interface point.
Note on C49: Select the type of neutral earthing. If "other" is selected, specify details in the "Additional notes" column. If "impedance earthed neutral" is selected, specify the value of impedance, current and duration in the "Additional notes" column.
Note on C50: Select the compatibility level for individual harmonic distortion of voltage in accordance with IEC 61000-2-4:2002, Table 2, Table 3, and Table 4. Default value : Class 2
Note on C51: Select the compatibility level for total harmonic distortion of voltage in accordance with IEC 61000-2-4:2002, Table 5. Default value : Class 2
Note on C53: Specify the nominal voltage of the auxiliary power at the interface point.
Note on C54: Select the source of auxiliary power supply. Default value : externally fed
Note on C55: Select the expected steady state voltage variation of the auxiliary power at the interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±10
Note on C56: Select the nominal frequency of the auxiliary power at the interface point. Default value : 50
Note on C57: Select the expected steady state frequency variation of the auxiliary power at the interface point. If "other" is selected, specify details in the "Additional notes" column. Default value : ±1
Note on C58: Specify the minimum and maximum short circuit current of the auxiliary power at the interface point.
Note on C59: Specify the type of neutral earthing. If "other" is selected, specify details in the "Additional notes" column. For "impedance earthed neutral", specify the value of impedance, current and duration in the "Additional notes" column.
Note on C60: Specify the expected maximum auxiliary power consumption of the proposed BESS.
Note on C62: Specify whether another language is to be used in addition to English for caution/danger/warning/safety marking information on equipment labels.
Note on C63: Select the acoustic noise at 1 m during operation in normal mode. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C64: Select whether the evidence/documentation detailing the supplier’s hazard identification process in accordance with IEC 62933-5-2 is required to be submitted. Default value : not required
Note on C65: Select whether evidence/documentation detailing the safety design and functional information for each risk reduction measure utilised in the supplier FMEA or FTA is required to be submitted. Default value : not required
Note on C67: Select the required BESS category in accordance with IEC 62933-5-2. If "other" is selected, specify details in the "Additional notes" column.
Note on C68: Select the intended purpose of the BESS application. If "other" is selected, specify details in the "Additional notes" column.
Note on C69: Specify the operation states of control for the selected BESS application.
Note on C70: Specify the rated active input power for which the BESS is to be designed to accept and store.
Note on C71: Specify the rated reactive input power for which the BESS is to be designed to absorb from the upstream network.
Note on C72: Specify the required rated active output power for which the BESS is to be designed to supply during its discharge phase.
Note on C73: Specify the required rated reactive output power for which the BESS is to be designed to supply during its discharge phase.
Note on C74: Specify the required rated energy storage capacity at the beginning of service life (BOL) for which the BESS is to be designed.
Note on C75: Specify the reference number of the BESS functional description document to be included as part of the BESS requisition.
Note on C77: Specify the reference of the duty cycle profile and description document to be included as part of the BESS requisition. Refer to Annex A and PNNL - 22010 for further guidance on the duty cycle use case definition and the parameters associated to it.
Note on C79: Specify the required lithium battery chemistry. If "other" is selected, specify details of lithium chemistry required in the "Additional notes" column. Default value : lithium iron phosphate - LFP (LiFePO4)
Note on C80: Select the required battery housing. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C81: Select the fire resistance rating for the battery housing. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C83: Select the PCS housing. If "other" is selected, specify details in the "Additional notes" column. Default value : manufacturer's standard
Note on C85: Select whether a fire suppression system for the battery housing is required. If "other" is selected, specify details in the "Additional notes" column. Default value : required
Note on C86: Select whether a fire and gas audible alarm is required. If "required" is selected, specify details (e.g. one audible alarm per container/cabinet or a common alarm for the entire BESS) in the "Additional notes" column. Default value : not required
Note on C88: Select the BESS message category for remote monitoring and control. Default value : category II
Note on C89: Select the network connectivity interface media based on time synchronization, remote access and configuration of the ECMS/PMS. If "other" is selected, specify details in the "Additional notes" column. Default value : Ethernet (fiber)
Note on C90: Select the required interface protocol to the ECMS/PMS as per project requirements. If "other" is selected, specify details in the "Additional notes" column. Default value : Ethernet IP
Note on C91: Select the interface network redundancy for the ECMS/PMS. If "other" is selected, specify details of the less preferred redundancy protocols such as the rapid spanning tree protocol (RSTP) as specified in IEEE 802.3 in the "Additional notes" column. Default value : not required
Note on C92: Select whether BESS remote access is required. Select "yes" if the BESS is to be accessed from a central location or a remote location through intranet or internet. Default value : yes - read only
Note on C93: Select the interface media for the external FGS. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C94: Select the interface protocol to the external FGS. If "other" is selected, specify details in the "Additional notes" column. Default value : not applicable
Note on C95: Select the interface media for the external ESD system. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C96: Select the interface protocol to the external ESD system. If "other" is selected, specify details in the "Additional notes" column. Default value : not applicable
Note on C97: Select whether hardware is required for remote access. If "required" is selected, specify details of hardware for interfacing with existing installations or third-party systems (e.g. adapters, connectors, cables) in the "Additional notes" column. Default value : required
Note on C99: Select whether interconnecting cables between BESS equipment or subsystems are required to be supplied as part of the BESS package. Default value : required
Note on C100: If interconnecting cables between BESS equipment or subsystems are required, specify the cable type required (e.g. 1.1kV/Cu/PVC/LSZH) and the applicable international standards.
Note on C102: Select whether the isolation or coupling transformer upstream of the BESS (PCS) is to be supplied as part of the BESS package. Default value : not required
Note on C103: Select whether the distribution transformer for externally fed auxiliary power supply of BESS is to be supplied as part of the BESS package. Default value : not required
Note on C104: Select whether the HV switchgear and associated devices upstream of the BESS (PCS) are to be supplied as part of the BESS package. Default value : not required
Note on C106: Select the transport, storage and handling requirements. If “other” is selected, specify details such as impact indicator, data logger, date-time stamping and export packing in the "Additional notes" column. Default value : manufacturer's standard
Note on C107: Select the required quantity of portable lifting trolley. If "other" is selected, specify details in the "Additional notes" column. Default value : not required

## Supplement
Row |  | IOGP S-753D (0.1) Procurement Data Sheet for Battery Energy Storage Systems (BESS) (IEC) | Issue
2 | PURCHASE ORDER SPECIFIC REQUIREMENTS
3 | Delete this sheet if not required
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
Public Review Draft

## Guidance
IOGP S-753D (0.1) Procurement Data Sheet for
Battery Energy Storage Systems (BESS) (IEC)
Guidance on the use of this procurement data sheet
To be used in conjunction with:
IOGP S-753 Supplementary Specification to IEC TS 62933-3-1 for Battery Energy Storage Systems (BESS).
This procurement data sheet is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This procurement data sheet, completed with requested values, should be delivered back to the purchaser by using the procurement data sheet template or other mutually agreed method.
Ref. Clause provides reference back to the parent standard or the supplementary specification where relevant.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the procurement data sheet item and/or an explanation of how to complete the input.
Additional notes may be used by the purchaser or supplier to provide additional information pertinent to the specification or supply of the equipment.
Issue should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the procurement data sheet that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data on a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the procurement data sheet. This worksheet is not intended to modify requirements defined in the specification.
Purchaser requirement and Purchaser requirement UOM specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
Supplier offered value and Supplier offered UOM are used by the supplier to declare the offered value. Where the offered product characteristic differs from the Purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the Purchaser requirement.
Requirement CFIHOS ID and Equipment CFIHOS ID are prepopulated and hidden in columns K and L of the procurement data sheet worksheet. The purpose of the CFIHOS IDs is to enable information exchange in a data-centric manner.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft