## Front & preliminaries
|  |  | SPECIFICATION | January 2025
|  |  | IOGP S-753L | Version 0.1
Information Requirements for Battery Energy Storage Systems (BESS) (IEC)
Revision history
VERSION | DATE | PURPOSE
0.1 | January 2025 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-753L (0.1) Information Requirements for Battery Energy Storage Systems (BESS) (IEC)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-753L (0.1) Information Requirements for Battery Energy Storage Systems (BESS) (IEC)
Introduction
The purpose of this information requirements specification (IRS) is to specify information requirements for the procurement of battery energy storage systems (BESSs) in accordance with IOGP S-753 for application in the petroleum and natural gas industries.
The IRS defines the information requirements, including format, timing and purpose, to be provided by the supplier. It also defines the specific conditions to be satisfied for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
The IOGP S-753 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), a procurement data sheet (PDS), this IRS and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Information Requirements Specification (IRS)
This IRS is to be applied in conjunction with the specification, the PDS and the QRS, referred to in this document as IOGP S-753, IOGP S-753D and IOGP S-753Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Instructions
IOGP S-753L (0.1) Information Requirements for Battery Energy Storage Systems (BESS) (IEC)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS structure contents
| 1 | 'Front & preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS discipline-document types.
Column E — 'Submit At Proposal' (Yes/No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information submission abbreviations
Column I — 'Required As Built' (Yes / No), where “Yes” chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS.
Column K — 'Translation Required' (Yes/No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment.
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PDS |  | procurement data sheet
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or “manufacturer”.
| TRS |  | technical requirements specification
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3. Metadata listed below is as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The unique identifier for the 'document' according to the 'owner/operator' document numbering scheme. |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document. |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised. |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision. |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision. |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision. |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision. |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Discipline document type short code |  |  | At alternate way of identifying uniquely a combination of discipline and document type. |  |  | CFIHOS-10000207
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification code |  |  | A code that uniquely identifies an export control classification. |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
Table 3 — Supplier deliverable metadata
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
IOGP S-753L (0.1) Information Requirements for Battery Energy Storage Systems (BESS) (IEC)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement.
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Document Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Requirements
S753-IR-1 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | - | - |  | -
S753-IR-2 | Delivery schedule |  | Delivery/Production schedule | Yes | For Acceptance |  | - | - |  | - | Preliminary delivery schedule to be submitted with proposal.
S753-IR-3 | Progress report |  | Progress report | No | For Information |  | - | - |  | -
S753-IR-4 | Quality plan |  | Quality plan | Yes | For Information |  | - | - |  | -
S753-IR-5 | Sub-vendor delivery schedule |  | Sub-supplier list | Yes | For Information |  | - | - |  | -
S753-IR-6 | Inspection and test plan for complete package |  | Inspection and test plan (ITP) | No | For Acceptance |  | - | - |  | -
S753-IR-7 | Handling, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | - | - |  | -
S753-IR-8 | Non-conformance records |  | Non-conformance records | No | For Information |  | - | - |  | -
S753-IR-84 | Technical deviation request |  | Deviation request | Yes | For Acceptance |  | - | - |  | -
S753-IR-9 | Concession requests |  | Concession request | Yes | For Acceptance |  | - | - |  | - | Proposal submission shall be a deviation list identifying the list of deviations to material requisition documents (TRS, PDS, IRS and QRS etc.)
S753-IR-82 | Sub-supplier list |  | Qualified supplier (vendor) list | Yes | For Information |  | - | - |  | -
Technical Information Requirements
S753-IR-54 | BESS overview, system description and architecture |  | Functional design specification | Yes | For Acceptance |  | - | - |  | -
S753-IR-55 | BESS control system description |  | Control system diagram | Yes | For Information |  | - | - |  | -
S753-IR-56 | BESS electrical protection description |  | Functional design specification | Yes | For Information |  | - | - |  | -
S753-IR-57 | BESS thermal management system (HVAC /Liquid cooling) description |  | Functional design specification | Yes | For Information |  | - | - |  | -
S753-IR-58 | BESS fire and gas system description |  | Functional design specification | Yes | For Information |  | - | - |  | -
S753-IR-59 | Battery Management System (BMS) description |  | Functional design specification | No | For Information |  | - | - |  | -
S753-IR-85 | Deflagration description and calculations |  | Functional design specification | No | For Information |  | - | - |  | -
S753-IR-26 | BESS equipment data sheets |  | Manufacturer data sheet | Yes | For Acceptance |  | - | - |  | - | The equipment data sheets submitted with the proposal should include all essential technical information necessary for bid analysis and evaluation.
S753-IR-27 | BESS single line diagram |  | Single line diagram | Yes | For Acceptance |  | - | - |  | -
S753-IR-48 | BESS equipment general arrangement drawings |  | General arrangement diagram | Yes | For Acceptance |  | - | - |  | - | Preliminary GA drawing to be submitted with proposal.
S753-IR-72 | BESS performance data and capability characteristic curves |  | Curves and tables calculations | Yes | For Information |  | - | - |  | -
S753-IR-68 | BESS electrical equipment sizing calculations |  | Design calculations | No | For Acceptance |  | - | - |  | -
S753-IR-60 | BESS equipment layout |  | Layout diagram | Yes | For Information |  | - | - |  | -
S753-IR-43 | BESS I/O schedule |  | Input, output list | No | For Information |  | - | - |  | -
S753-IR-25 | BESS reliability and availability |  | Reliability, availability, safety integrity level calculation | Yes | For Information |  | - | - |  | -
S753-IR-81 | Hazard identification, risk analysis and risk reduction measures |  | Failure mode effect and criticality analysis report (FMECA) | No | For Information |  | - | - |  | - | This documentation will be submitted only when requested in the PDS, otherwise not required.
S753-IR-67 | Battery sizing calculation |  | Design calculation | Yes | For Acceptance |  | - | - |  | -
S753-IR-44 | Input data for harmonic analysis |  | System study | Yes | For Information |  | - | - |  | -
S753-IR-78 | Arc flash calculations and hazard assessment |  | Hazard Analysis | Yes | For Information |  | - | - |  | -
S753-IR-62 | Cable list/schedule |  | Cable list | Yes | For Information |  | - | - |  | - | Submit at proposal when interconnecting cables between BESS equipment or subsystems are required to be supplied by the BESS supplier.
S753-IR-66 | Utility summary, consumption data and electrical load list |  | Consumption data and load list | Yes | For Information |  | - | - |  | -
S753-IR-73 | Power system study data |  | System study | No | For Information |  | - | - |  | -
S753-IR-69 | Communication Interface diagram |  | Interface diagram | No | For Acceptance |  | - | - |  | -
S753-IR-64 | Container fabrication drawings |  | Detailed drawing | No | For Information |  | - | - |  | -
S753-IR-63 | Foundation loading diagram (static & dynamic) |  | Foundation loading diagram | No | For Acceptance |  | - | - |  | -
S753-IR-28 | Termination diagram |  | Termination diagram | No | For Acceptance |  | - | - |  | -
S753-IR-29 | Wiring diagram |  | Wiring diagram | No | For Information |  | - | - |  | -
S753-IR-61 | Schematic diagram |  | Schematic diagram | No | For Information |  | - | - |  | -
S753-IR-24 | BESS heat dissipation summary |  | Heat dissipation calculation and loads | Yes | For Information |  | - | - |  | - | A preliminary value of the BESS heat dissipation is needed at proposal stage to support the design of HVAC sizing.
S753-IR-65 | Earthing diagram |  | Earthing diagram | No | For Information |  | - | - |  | -
S753-IR-74 | Lighting layout |  | Layout diagram | No | For Information |  | - | - |  | - | This document is applicable only for walk-in type containers.
S753-IR-30 | Bill of materials |  | Bill of materials | No | For Information |  | - | - |  | -
S753-IR-31 | Consolidated spare parts list |  | Consolidated spare parts list | No | For Information |  | - | - |  | -
S753-IR-79 | Special tools list |  | Special tools list | No | For Information |  | - | - |  | -
S753-IR-32 | Commissioning instruction |  | Commissioning instruction | No | For Information |  | - | - |  | -
S753-IR-33 | Installation manual |  | Installation manual | No | For Information |  | - | - |  | - | Installation Manual index, if required, should be provided in first revision of the document. When index agreed, Installation manual content shall be provided in subsequent revision of the document. Can be accepted as a combined installation, operation and maintenance manual.
S753-IR-34 | Maintenance manual |  | Maintenance manual | No | For Information |  | - | - |  | - | Maintenance manual index, if required, should be provided in first revision of the document. When index is agreed, maintenance manual content shall be provided in subsequent revision of the document. Can be accepted as a combined installation, operation and maintenance manual.
S753-IR-36 | Operating manual |  | Operating manual | No | For Information |  | - | - |  | - | This document can be accepted as a combined installation, operation and maintenance manual.
S753-IR-37 | Factory acceptance test (FAT) procedure |  | Factory acceptance test (FAT) procedure | No | For Acceptance |  | - | - |  | -
S753-IR-38 | Site acceptance test (SAT) procedure |  | Site acceptance test (SAT) procedure | No | For Acceptance |  | - | - |  | -
S753-IR-39 | Factory acceptance test (FAT) records |  | Factory acceptance test (FAT) records | No | For Acceptance |  | - | - |  | -
S753-IR-40 | Site acceptance test (SAT) records |  | Site acceptance test (SAT) records | No | For Acceptance |  | - | - |  | -
S753-IR-42 | Type test certificate |  | General certificate | No | For Information |  | - | - |  | - | CAS A, B and C - For acceptance and submission at proposal stage : CAS D - For information.
S753-IR-41 | Manufacturer record book (MRB) |  | Manufacturer record book (MRB) | No | For Information |  | - | - |  | - | Manufacturer Record Book index, if required, shall be provided in first revision of the document. When index agreed, Manufacturer Record Book content shall be provided in subsequent revision of the document.
S753-IR-45 | Hazardous area certificate | Required only for hazardous area certified equipment and component | Hazardous area certificate | No | For Information |  | - | - |  | -
S753-IR-35 | Obsolescence management plan |  | Obsolescence management plan | Yes | For Information |  | - | - |  | - | "CAS A: For acceptance (before start of manufacturing), CAS B: For information, CAS C: For information, CAS D: for information".
S753-IR-47 | Packing list |  | Packing list | No | For Information |  | - | - |  | -
Purchase Order Specific Information Requests
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
IOGP S-753L (0.1) Information Requirements for Battery Energy Storage Systems (BESS) (IEC)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Requirements
S753-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the [Vendor] and accepted by the [Purchaser] to meet the information requirements defined in the agreed Information Requirements Specification (IRS). The schedule typically defines; a. information deliverable type, title/description b. unique identification (code/number) in the [Vendor's] format unless agreed otherwise in the contract. c. planned submission arrangements including; purpose, formats, timing, frequency Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. |  | Native | CFIHOS-70000099
S753-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by [vendor/sub-vendors]. Schedule details typically** include; a) Contractual milestones b) Activity early/late start/completion dates, durations, dependencies (Calendar Dates) c) Critical path and float d) Outsourced services and equipment (cross referenced to purchase order and supplier) e) Information deliverable submission dates identifying any execution activity dependencies Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. ** Schedule development tools, formats and submission protocols follow the [vendor's] standard practice unless otherwise agreed in the contract. |  | Native | CFIHOS-70000298
S753-IR-3 | Progress report | Report detailing activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities. Note: may also include actionable items such as Health, Safety, Security & Environment (HSSE) incidents & status if required under the Contract. |  | PDF | CFIHOS-70000300
S753-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. [API Spec Q2 may be used to inform the development of Service Quality Plans] |  | PDF | CFIHOS-70000451
S753-IR-5 | Sub-vendor delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the [vendor] to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the Contract or Quality Requirements Specification (QRS). Note: ISO 9001, API Specs Q1/Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | PDF | CFIHOS-70000455
S753-IR-6 | Inspection and test plan for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated [vendor], [purchaser] and independent conformity assessment activities. ISO 9001 Clause 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. |  | PDF | CFIHOS-70000180
S753-IR-7 | Handling, shipping, storage and preservation procedure | Definition of practices to be followed during the; storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements; package description, contents, identification, size, weight and number of packages/container (s), b. special packing/unpacking/handling requirements c. storage location and condition requirements, d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning. e. external auxiliary power supply connections for space heaters. f. recommended ambient conditions for the storage. g. requirement such as impact indicator, data logger and date-time stamping and export packing etc. | 12.1, 12.2, 12.4, 12.5, B.3 | PDF | CFIHOS-70000154
S753-IR-8 | Non-conformance records | Details of non-conformances raised by or to the [vendor/sub-vendors] against technical requirements during or after factory acceptance testing or prior to or during the delivery of the products or services. Non-conformance is managed by the [vendor] in accordance with ISO 9001 Clause 8.7 and associated records typically include; description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. Note: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the [purchaser] in accordance with the concession management protocols defined in the Contract. |  | PDF | CFIHOS-70000226
S753-IR-84 | Technical deviation request | A request, approval or rejection of changes to a technical specification. Would typically include justification and reasons for the request, and acceptance or rejection from a purely technical perspective. Synonym: Concession, Change Request. |  | - | CFIHOS-70000389
S753-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept the product, or service, that does not conform to ​​​​​​the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout. |  | PDF | CFIHOS-70000389
S753-IR-82 | Sub-supplier list | A list of suppliers qualified to deliver a specific scope, products and/or services. |  | PDF | CFIHOS-70000014
Technical Information Requirements
S753-IR-54 | BESS overview, system description and architecture | The overview, system description, and architecture document describe the technical aspects of BESS, ensuring proper design, implementation, and operation. It combines high-level overviews with detailed descriptions and architectural diagrams, serving as a foundation for project development. | 1, 4.2.4, 5.5.5, 6.2.3.1, 5.1, 5.3.1, 5.4.2, 5.5.1.2, 5.5.2, 5.5.3, 5.5.4, 5.5.9.2, 5.5.9.4, 5.5.9.5, 5.6.2, 5.6.3.1, 5.6.3.3, 5.8.1, 5.8.2, 7.1 | PDF | CFIHOS-70000244
S753-IR-55 | BESS control system description | The control system description document describes how the various control systems work together to monitor, manage, and optimise the performance of the BESS, ensuring safe and efficient operation under different operating conditions. | 1, 4.2.4, 5.5.5, 5.3.1, 5.4.2, 5.5.1.2, 5.5.2, 5.5.3, 5.5.4, 5.5.9.2, 5.5.9.4, 5.5.9.5, 5.6.2, 5.6.3.1, 5.6.3.3, 5.8.1, 5.8.2, 7.1, 7.6 | PDF | CFIHOS-70000066
S753-IR-56 | BESS electrical protection description | This document describes the safeguarding requirements for the BESS to protect against faults, overloading, abnormal conditions, and potential hazards such as short circuits, overvoltages, or ground faults. The primary goal of the protection system is to prevent damage to the BESS components, ensure safe operation, and minimize downtime during fault conditions. | 1, 4.2.4, 5.5.5, 5.5.1.2, 5.5.2, 5.5.3, 5.5.4, 5.5.9.2, 5.5.9.3, 5.5.9.4, 5.5.9.5, 5.7.1.1, 5.7.1.2, 5.7.1.3, 5.8.1, 5.8.2, 7.1 | PDF | CFIHOS-70000244
S753-IR-57 | BESS thermal management system (HVAC /Liquid cooling) description | The document typically describes how heating, ventilation, and cooling systems, are integrated into the BESS to maintain optimal operating temperatures and prevent overheating or thermal runaway. | 1, 4.2.3, 5.2.3.3, 5.5.1.2, 5.5.9.3, 5.8.1, 5.8.2, 7.1, 8.3.1.10, 9.2.2, 9.2.3, 9.2.4, 9.2.5, B.2 | PDF | CFIHOS-70000244
S753-IR-58 | BESS fire and gas system description | The fire and gas system description document describes the design, layout, functionality, and operation of the fire detection, suppression (where requested), off-gas monitoring and detection systems within the BESS. Given the safety risks associated with energy storage systems, especially the risk of thermal runaway in batteries and the potential release of flammable gases, this document ensures that appropriate fire and gas protection measures are in place to safeguard the system, personnel, and the surrounding environment. | 1, 4.2.3, 5.5.1.2, 5.5.3, 5.5.9.3, 5.8.1, 5.8.2, 7.1, 8.3.1.11, 8.3.1.12, 8.4.5, 8.4.6, 9.1.1, 9.1.2, 9.1.3, 9.1.4, 9.1.5, 9.1.6, 9.1.7, B.2 | PDF | CFIHOS-70000244
S753-IR-59 | Battery Management System (BMS) description | This document describes the design, architecture, and functionalities of the Battery Management System (BMS) employed in the BESS. It focuses on the BMS's role in monitoring and managing battery performance while ensuring the safety, efficiency, and longevity of the battery cells within the system. | 5.4.2, 5.5.1.2, 5.8.1, 5.8.2, B.2 | PDF | CFIHOS-70000244
S753-IR-85 | Deflagration description and calculations | A diagram showing the precise location of the deflagration unit, and sizing calculations to demonstrate capability to safely mitigate the explosion blast pressure. |  | - | CFIHOS-70000244
S753-IR-26 | BESS equipment data sheets | Document providing information on technical data and characteristics about material, products or systems and their environment for proper implementation. This document provides structured data form containing part number/model, design information, operational data and limitations of the equipment including cable length limitations (if any) for the selected communication interface. An individual data sheet for each equipment of the BESS, or a comprehensive data sheet that includes information for all equipment within the BESS is required. | 4.2.1, 5.2.2.4, 5.2.4.2, 5.5.5, 4.1, 4.2.2, 5.1, 5.2.2.1, 5.2.2.2, 5.2.3.2, 5.2.3.3, 5.2.3.4, 5.2.3.5, 5.2.3.6, 5.3.1, 5.4.2, 5.4.3, 5.4.4, 5.4.6, 5.4.8, 5.5.1.2, 5.5.1.4, 5.5.2, 5.6.2, 5.7.1.1, 5.7.1.2, 5.7.1.3, 7.6, 7.7, 7.8, 7.9, 8.2.3, 8.3.1.10, 8.3.1.11, 8.3.1.12, 8.3.1.2, 8.3.1.8, 8.4.1, 8.4.2, 8.4.4, 8.4.5, 8.4.6, 8.4.8, 9.2.5, A.3.2, B.2 | PDF | CFIHOS-70000416
S753-IR-27 | BESS single line diagram | A diagram depicting all key electrical equipment of the BESS (e.g. power conversion system, battery, DC distribution, auxiliary power distribution and their isolation devices/components) with their voltage, current and fault withstand ratings along with the points of interface for both the main power system and the auxiliary power connections. | 4.2.2, 5.7.1.1, 5.7.1.2, 5.7.1.3, 7.8, 7.9 | PDF | CFIHOS-70000371
S753-IR-48 | BESS equipment general arrangement drawings | A drawing showing overall dimensions, critical interface dimensions, part references and weight of the BESS assemblies, equipment and components. This drawing contains reference to main specifications and standards. For equipment/components the drawing may include cross sectional views. Document typically contains the following information: — main dimensions — internal arrangement of components & terminations — interface connections — marking, labelling, nameplate and rating plate information — weight — centre of gravity — withdrawal/installation and maintenance space — sectionalization and transportation unit — installation and mounting details — lifting arrangement — quantity of assemblies/equipment/components, if more than one supplied. | 5.7.3.2, 7.2, 7.5, 7.8, 7.9, 8.2.1, 8.2.3, 8.3.1.13, 8.3.1.15, 8.3.1.16, 8.3.1.9, 8.3.2.1, 8.3.2.2, 8.3.2.3, 8.4.1, 8.4.10, 8.4.11, 8.4.12, 8.4.13, 8.4.14, 8.4.4, 8.4.5, 8.4.6, 8.4.7, 9.2.1, B.2 | PDF | CFIHOS-70000153
S753-IR-72 | BESS performance data and capability characteristic curves | This document describes the main characteristic and limits of the BESS. This document provides information to be used into system engineering characteristics and functional parameters with probable performance shown. Document includes but is not limited to calculations, curves, tables, reference to similar applications and test data. This as a minimum is at a level customary for the equipment and to the extent such data are of importance for interfaces to plant and system. The BESS performance data to be included in this documentation provides, at a minimum, provide the following information: – System response time – Roundtrip efficiency – System ramp rate capability (% of rated output power) – Short-circuit current contribution – Voltage ride-through capability (LVRT / OVRT) – P(f) regulation characteristic – Q(U) capability – Self-discharge rate – Energy capacity – Input and output power BESS recovery process characteristics to be included in this documentation provides, at a minimum, the following information: – Minimum duration of recovery – Maximum duration of recovery – Allowable range (maximum / minimum) of active output power (% of rated active output power) – Maximum allowed ramp rate of reactive output power (% of rated reactive output power) – Allowable range of power factor at the power system interface. | 5.1, 5.4.2, 5.4.3, 5.8.1 | PDF
S753-IR-68 | BESS electrical equipment sizing calculations | Document providing information about data, and basic conditions and assumptions used for selection of appropriate equipment (e.g. power conversion system, transformer or power distribution equipment), parts or material, as well as the way these data have been processed and evaluated. Mandatory content of information: – Calculation methods used; – Input data; – Results; – Analysis of the results. Optional content of information: – Case studies; – Verification of different technical solutions. | 4.1, 5.1, 5.2.1, 5.2.2.1, 5.2.3.3, 5.3.1, 5.4.1, 5.4.2, 5.4.3, 5.4.8 | PDF | CFIHOS-70000086
S753-IR-60 | BESS equipment layout | A BESS Layout Document is a detailed technical drawing that provides the physical arrangement and spatial organisation of the equipment/components within the BESS. This document may include an overall layout when multiple BESS arrays are supplied, providing a clear view of how the arrays and related equipment/components are positioned within the system. | 5.8.1, 7.1, 9.2.1, 9.2.2, 9.2.3, 9.2.4 | PDF | CFIHOS-70000277
S753-IR-43 | BESS I/O schedule | A list identifying all input and output signal (soft and hard wired) interfaces between functional units of the BESS and other external equipment. Mandatory content of information required: mapping addresses for the data communication and signaling circuits intended to be exchanged between functional units of the BESS and other external equipment / systems (e.g. ECMS, PMS, FGS or ESD). | 5.6.1, 9.1.7 | PDF | CFIHOS-70000179
S753-IR-25 | BESS reliability and availability | Demonstrates starting and operating reliability / availability of the BESS (e.g. mean time between failure data). | 5.1, 7.1 | PDF | CFIHOS-70000312
S753-IR-81 | Hazard identification, risk analysis and risk reduction measures | BESS hazard identification and risk analysis documentation detail the supplier’s hazard identification process as per IEC 62933-5-2 and BESS system level risk analysis using one of the following techniques, or equivalent: - Failure Modes and Effect Analysis (FMEA) - IEC 60812. - Fault Tree Analysis (FTA) – IEC 61025. BESS risk reduction measure documentation details the safety design and functional information for each risk reduction measure utilised in the Supplier FMEA or FTA, including but not limited to: - results of UL 9540A fire and explosion testing - calculations or modelling to determine compliance with NFPA 68 for deflagration. - other test and/or design/calculation data such as functional requirements for active electrical, electronic and software risk reduction measures (e.g., ESMS, BMS). Functional safety management as per IEC 61508 (all parts) is part of this documentation where fire, explosion or toxic gas discharge is identified as a risk. | 5.1, 7.1 | PDF | CFIHOS-70000436
S753-IR-67 | Battery sizing calculation | Document providing information about data, and basic conditions and assumptions used for the battery sizing of the BESS, as well as the way these data have been processed and evaluated. Mandatory content of information: – Calculation methods used; – Input data; – Results; | 4.1, 4.2.1, 5.1, 5.2.1, 5.2.3.3, 5.3.1, 5.4.1, 5.4.2, 5.4.3, 5.4.8, 5.8.1 | PDF | CFIHOS-70000086
S753-IR-44 | Input data for harmonic analysis | This document provides comprehensive harmonic data (spectrum) for the connected BESS, enabling power system engineers to analyse the impact of total harmonics on the overall power system. | 5.2.2.3 | PDF | CFIHOS-70000388
S753-IR-78 | Arc flash calculations and hazard assessment | Arc flash calculations and hazard assessment for BESS follow industry-standard methods but involve additional considerations due to the presence of high-energy DC circuits and complex power conversion systems. These calculations assess the potential arc flash energy and help define the necessary personal protective equipment (PPE) and safety measures. | 5.8.1, 7.8, 7.9 | PDF | CFIHOS-70000155
S753-IR-62 | Cable list/schedule | A collection of values relating to List of all cables, their specifications (voltage grade, cable type and size etc.) and end points. Indicates salient features of all cables in Vendor's supply and connecting cables supplied by Principal. Synonym: Cable Schedule | 5.7.3.1, 5.7.3.2 | PDF | CFIHOS-70000033
S753-IR-66 | Utility summary, consumption data and electrical load list | Document providing input to engineering for design of the customer's installation or utility arrangement, stating the normal and maximum consumption of e.g. heating/cooling media, electrical power, etc., for the equipment or unit(s). The following generalized index shall be used: — equipment tag no; — type of utility; — utility consumption figures, for example: Consumer description, type of load, load factors, approximate power consumption data in operation and standby mode. | 5.1, 5.4.4 | PDF | CFIHOS-70000203
S753-IR-73 | Power system study data | This deliverable outlines the necessary data for the power system study, which will be carried out by others. BESS power system model – A configured software model of the BESS package, created using commercially available power systems analysis software approved by the Purchaser. This model will be integrated into the main power system model developed by others to facilitate the completion of the following studies. | 5.5.1.4 | PDF | CFIHOS-70000388
Steady-state load-flow;
Short-circuit;
Root Mean Square (RMS) transient stability;
Harmonic analysis;
Motor starting.
BESS model user guide – This guide provides a comprehensive description of the BESS power system model, instructions on how it should be integrated into the plant power system model, and guidelines for tuning BESS parameters for optimisation of power system performance. Power study input data – This outlines all other the input data necessary for conducting comprehensive power system studies, such as load flow, short circuit, harmonic and stability analysis [e.g. harmonic spectrum data, interface cable data etc].
S753-IR-69 | Communication Interface diagram | A diagram documenting Interfaces and demarcation of responsibilities between different organizations (e.g. battery limits, terminations). A BESS Communication Interface Diagram is a graphical representation that illustrates the communication pathways, protocols, and interactions between various components and systems within the BESS and with external equipment / systems (e.g. ECMS, PMS, FGS or ESD). | 4.2.4, 5.6.2, 5.6.3.1, 5.6.3.3 | PDF | CFIHOS-70000186
S753-IR-64 | Container fabrication drawings | This document describes the structural and lifting details of the structural elements, connection details and precise details of fixed pad eyes used for installation and maintenance. Details of any temporary lifting beams or spreader frames with limits on sling angles and loads are to be clearly identified. | 8.3.1.1, 8.3.1.5, 8.3.1.6, 8.3.2.2, B.2 | PDF | CFIHOS-70000438
S753-IR-63 | Foundation loading diagram (static & dynamic) | A diagram detailing static and dynamic forces or movements acting on foundations or other load bearing supports. May include Civil Structural for loads imposed, and Civil Foundations for foundation design. | B.1, Table 5 | PDF | CFIHOS-70000151
S753-IR-28 | Termination diagram | A diagram for the main and auxiliary power equipment, power conversion system, battery, and other components of the BESS identifies all connections and cable terminations at the input and output power terminal connection points. This diagram is required for removal, hookup, and modification purposes, and should include all vendor interface points. | 5.7.2.1, 5.7.2.2, 5.7.2.3 | PDF | CFIHOS-70000330
S753-IR-29 | Wiring diagram | A diagram providing detailed information on the circuitry of all key electrical equipment of the BESS (e.g. power conversion system, battery, DC distribution, auxiliary power distribution). Mandatory content of information required: — graphical symbols representing the objects; — graphical symbols representing the connections among objects; — reference designations; — terminal designations; — signal level conventions (applicable to logic signals); — information necessary to trace paths and circuits (signal designations, location references); — supplementary information necessary for the understanding of functions; — references to other documents; — information about wiring logic; — cable and cable core identification; — maximum cross section area and number of runs of power cables; — user interfaces (wiring connection with other equipment); — cable length limitations (if any) for the selected communication interface. | 4.2.1, 4.2.2, 4.2.3, 4.2.4, 5.7.1.1, 5.7.1.2, 5.7.1.3, 5.7.2.1, 5.7.2.2, 5.7.2.3, 7.8, 7.9 | PDF | CFIHOS-70000268
S753-IR-61 | Schematic diagram | A diagrammatic representation of all essential electrical equipment (such as the power conversion system, battery, DC distribution, and auxiliary power distribution) of the BESS, illustrating their functions along with input/output sources (e.g., circuit breakers, switches, relays, etc.) and their interconnections. The diagram includes details of the logic functions governing the circuit. | 4.2.1, 4.2.2, 4.2.3, 4.2.4, 5.7.2.1, 5.7.2.2, 5.7.2.3, 7.8, 7.9 | PDF | CFIHOS-70000328
S753-IR-24 | BESS heat dissipation summary | This document contains the calculation by the manufacturer to arrive at the heat load produced by the equipment to enable HVAC sizing. | 4.2.3, 5.2.3.3, 9.2.1, 9.2.2, 9.2.3, 9.2.4 | PDF | CFIHOS-70000441
S753-IR-65 | Earthing diagram | This diagram provides details on how electrical assembilies/equipment/components within the BESS are connected to the earth to ensure safety, protect equipment, and prevent electrical faults. | 8.3.1.13, 8.3.1.14, 8.3.1.15, 8.3.1.16, 8.4.10, 8.4.11, 8.4.12, 8.4.13, 8.4.14 | PDF | CFIHOS-70000103
S753-IR-74 | Lighting layout | This is a technical drawing that outlines the placement and design of lighting systems within the BESS installation. | 8.3.2.6, 8.3.2.7, 8.3.2.8 | PDF | CFIHOS-70000277
S753-IR-30 | Bill of materials | A list of parts, components and sub-assemblies of the BESS, including part numbers, item numbers, quantities, material designations and technical specifications. Note: This document includes details of sub-suppliers & items of associated purchase orders. | 10.1, 10.2, 11, 5.7.3.1 | PDF | CFIHOS-70000028
S753-IR-31 | Consolidated spare parts list | A table containing the items specifying the objects (parts, components, software, equipment, etc.) of the BESS that are available or delivered as spare parts for later use. Mandatory content of information: – Item reference number; – Quantity; – Part number or global identifier (together with manufacturer / supplier); – Part name. Optional content of information: – Type designation; – Specifying technical data; – Descriptive technical data; – Mass, dimensions; – Reference to document; – Remark. A consolidated spare parts list generated to support the execution of project purchasing for the purpose of commissioning, start-up, maintenance support, etc, also widely known as Spare Part List and Interchangeability Record (SPIR). | 5.3.1, 5.4.9 | PDF | CFIHOS-70000420
S753-IR-79 | Special tools list | This document identifies all special tools necessary for handling, dismantling, maintenance etc. of equipment. This document is a part of the Spare part list and includes: • Identification - the tag number the special tool supports • Description of the special tool • Storage, i.e. the location where the special tool can be found • Document references, if applicable Note that the actual special tool includes the identification marking, i.e. tag number that it supports. | 5.3.1, 5.4.9 | PDF | CFIHOS-70000454
S753-IR-32 | Commissioning instruction | Instructions detailing the commissioning process of the BESS. These instructions are particularly focused on large and complex parts, components, and equipment involved in the BESS installation. The purpose of these instructions is to guide the user with the necessary information for the initial setup of the BESS. These instructions typically contains: — download program, software instructions; — checking instructions; — checks to be performed before connection to the supply network and before first operation; — details of specifications to apply to acceptance, inspection and performance tests. | 6.2.3.1 | PDF | CFIHOS-70000396
S753-IR-33 | Installation manual | A description of methods of installing the BESS. Installation refers to the mounting, setting, erection, etc. of the parts, components, and equipment involved in the BESS installation. Note: Unless otherwise agreed, this document can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a standalone document. | 6.2.3.1 | PDF | CFIHOS-70000181
S753-IR-34 | Maintenance manual | A description of methods of maintaining the parts, components, and equipment involved in the BESS. The maintenance manual includes the mechanical handling plan in accordance with ISO 11228 (all parts). Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard installation, operation and maintenance manual or as a standalone document. This document confirms: — the lifetime of the electronic components / controls; — the availability of spare parts; — the expected duration of the replacement process; — the availability of software support during the lifetime of the equipment. | 5.3.1, 5.4.9 | PDF | CFIHOS-70000206
S753-IR-36 | Operating manual | A description of the methods for operating the parts, components, and equipment involved in the BESS. This includes, but is not limited to, instructions, procedures, drawings, and tables. The description will cover operational limits, function testing, potential interruptions, corrective actions, hazards, and the necessary measures to address them. Note: Unless otherwise agreed, can be delivered as part of manufacturer's standard Installation, operation and maintenance manual or as a stand alone document. | 5.3.2 | PDF | CFIHOS-70000228
S753-IR-37 | Factory acceptance test (FAT) procedure | The FAT procedure is used to ensure a common understanding of performed testing and acceptance criteria. This document includes all testing activities and their acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. This document defines the test set-up and test equipment. The FAT procedure includes the functional testing requirements for the BESS subsystems (FGS, Thermal Management, and BMS), based on the respective system descriptions submitted by the BESS supplier. | 4.2.1, 6.1, 7.1, 8.1, B.2 | PDF | CFIHOS-70000427
S753-IR-38 | Site acceptance test (SAT) procedure | Procedure documenting the manufacturers recommended site tests including discrete functional unit and overall system, interlocks (electrical, mechanical), interfaces, protection and communications. The SAT procedure includes the functional testing requirements for the BESS subsystems (FGS, Thermal Management, and BMS), based on the respective system descriptions submitted by the BESS supplier. | 6.1 | PDF | CFIHOS-70000428
S753-IR-39 | Factory acceptance test (FAT) records | The FAT report is used to verify that the equipment has been tested according to FAT procedure. The FAT report is used for acceptance of the equipment delivery. This document includes all testing activities and their acceptance criteria, in accordance with the FAT procedure, to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. This document defines test set-up and test equipment. | 4.2.1, 6.1, B.2, Table 9 | PDF | CFIHOS-70000429
S753-IR-40 | Site acceptance test (SAT) records | Records demonstrating results of site tests including discrete functional unit and overall system, interlocks (electrical, mechanical), interfaces, protection and communications. | 6.1 | PDF | CFIHOS-70000430
S753-IR-42 | Type test certificate | A document providing objective evidence that the equipment is compliant to relevant standards. To include equipment designation, manufacturer, testing authority name and address, specific year and edition of the standards (IEC,UL and UN) adopted to perform verification and a summary of the proving tests performed. | 7.1, 8.1, 8.2.2, 8.3.1.1, Table 9 | PDF | CFIHOS-70000239
S753-IR-41 | Manufacturer record book (MRB) | Detailed information/description for the documents to be included in MRB as agreed between Purchaser and Vendor. MRB typically includes but is not limited to documents Recording Compliance With Statutory and/or Local Regulations, and inspection and testing results / reports for all the testing carried out at Vendor/Sub-Vendor shop. | B.3 | PDF | CFIHOS-70000178
S753-IR-45 | Hazardous area certificate | Attestation issued by a recognised independent authority certifying that a type test has satisfied the requirements of the standards; e.g. ATEX, BASEEFA, PTB, UL, CSA, NEMA, EX, etc. Examples of ratings include Intrinsically Safe & Flame Proof enclosures, any special requirements for safe use, barrier/isolator to be used, etc. | 7.1 | PDF | CFIHOS-70000160
S753-IR-35 | Obsolescence management plan | The supplier to submit an obsolescence management plan in accordance with IEC 62402 for the BESS. The plan will provide milestone dates such as end of production (EOP) and also predicted end of supply. | 5.3.1, 5.4.9 | PDF | CFIHOS-70000447
S753-IR-47 | Packing list | A list describing the contents of a shipment received. Synonyms: Inventory, packing slip, bill of landing. | 12.1, 12.2, B.3 | PDF | CFIHOS-70000269
Purchase Order Specific Information Requests
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Back cover
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Document Type Code
Hard Copy
Native
PDF
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: