## Guidance
S-719D Data Sheet for
Water Mist Fire Protection
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-719 Supplementary Specification to NFPA 750 Standard on Water Mist Fire Protection.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) are pre-populated in this data sheet, but may be modified as required by the user.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the datasheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
IOGP S-719D Version 0.1
Public Review Draft

## Front & Preliminaries
|  |  |  | SPECIFICATION | October
|  |  |  | S-719D | 2019
Data Sheet for
Water Mist Fire Protection
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | October 2019 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Project 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-719D Version 0.1
S-719D Data Sheet for
Water Mist Fire Protection
Foreword
This specification was prepared under a Joint Industry Programme 33 (JIP33) “Standardization of Equipment Specifications for Procurement” organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization for projects globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly approved specification, building on recognized industry and/or international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages, facilitating improved standardization of major projects across the globe. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focussed standardisation initiatives and provide step change benefits in the sector’s capital projects performance
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP’s Competition Law Guidelines (November 2014).
IOGP S-719D Version 0.1
S-719D Data Sheet for
Water Mist Fire Protection
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the supply of water mist fir protection systems, in accordance with IOGP S-719, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-719, information requirements specification IOGP S-719L and quality requirements specification IOGP S-719Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
IOGP S-719D Version 0.1
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## General
Row | S-719D Data Sheet for Water Mist Fire Protection | [8 empty] | Issue
2 | Tag No. : |  | Insert Tag Number
3 | Service : |  | Insert Service Description | [7 empty] | Default
4 | Ref. Clause | Description | Requirement | [5 empty] | Additional notes
5 |  | Manufacturer : | [5 empty] | Input Data | Confirm water mist system manufacturer
6 |  | Project number : | [5 empty] | Input Data | Confirm project number
7 |  | Project name : | [5 empty] | Input Data | Confirm project name
8 |  | Project Documentation : | [5 empty] | Input Data | Confirm details of drawings for the protected items/spaces
9 |  | Installation country (site) : | [5 empty] | Input Data | Advise the country and site for final installation of the system.
10 |  | End user/ final client : | [5 empty] | Input Data | Purchaser to advise
11 |  | RFQ number : | [5 empty] | Input Data | Confirm RFQ number
12 |  | Tag number : | [5 empty] | Input Data | Indicate the unique tag number for the Water Mist Fire Fighting System based on PID.
13 |  | Order status : | [5 empty] | Select | Advise order status, this shall allow both purchaser and manufacturer to more accurately define values as they become available. |  | Select | For enquiry | For purchase
14 | 4.1.1.2, 4.1.1.3 | Limitations of use : | [5 empty] | Select | Purchaser to confirm that the protected items/spaces do not include those listed in 4.1.1.2 and 4.1.1.3 |  | Select | Confirm | Unknown
15 |  | Conformity Assessment System : | [5 empty] | Select | Select CAS level as applied in S-719Q, Annex A |  | Select | A | B | C | D
16 |  | Product delivery (purchaser) : | [5 empty] | Input Data | Purchaser to advise on required delivery date for the water mist system.
17 |  | Product delivery (supplier) : | [5 empty] | Input Data | Supplier to confirm delivery date of water mist system
18 | 17.1.5, 17.8.1, 8.5.6.6.2 | Location Environment : | [5 empty] | Select | Purchaser to confirm final location environment. |  | Select | Onshore – Coastal | Onshore – Desert | Onshore – Inland | Offshore – Fixed | Offshore – Floating | Marine (Ship)
19 | 8.5.4 | Blast protection consideration : | [5 empty] | Input Data | To clarify if the fire fighting skid is subject to blast protection requirements, purchaser to clarify severity/rating.
20 | 6.2.2.1, 6.5.7.1, 8.3.7 | Seismic consideration : | [5 empty] | Input Data | To clarify if geographical location is subject to seismic activity, severity/rating to be defined.
21 | 17.1.5, 17.8.1, 6.1.3.1, 6.6.4, 6.6.5, 8.1.3, 8.5.4 | Corrosive Atmospheres. : | [5 empty] | Input Data | Clarify if any parts of the water mist system could be subjected to severe corrosive atmospheres,
22 | 17.8.1 | Altitude : |  |  |  |  | Select | m | Advise maximum altitude which the water mist system shall operate at |  | Select | <1000 | >1000 | other
23 | 12.5.1.1, 12.5.1.2, 12.5.1.3 | Water Quality : | [5 empty] | Input Data | Purchaser to define water quality available at final installation site
24 | 17.8.1, 6.10.3.4 | Minimum ambient air temperature : |  |  |  |  | Select | ºC | Advise minimum ambient air temperature which the system can encounter. Note: Temperatures outside of 4 to 54 ºC may require additional design considerations. |  | Select | 4 | 0 | -15 | -20 | below -20 | other
25 | 17.8.1, 6.10.3.4 | Maximum ambient air temperature : |  |  |  |  | Select | ºC | Advise maximum ambient air temperature which the system can encounter. Note: Temperatures outside of 4 to 54 ºC may require additional design considerations. |  | Select | 40 | 45 | 50 | 54 | other
26 | 12.5.4.3, 17.7, 8.1.3, 8.1.4, 8.3.7, 8.5.4 | FFS Enclosure (Fire Fighting Skid) : | [5 empty] | Select | Select if the pump/cylinder unit (water delivery) is to be protected by an enclosure. Define the criteria from severe weather conditions or to mechanical, chemical, or other damage such as blast protection. |  | Select | Yes | No
27 |  | Transport and storage conditions : | [5 empty] | Select | Manufacturer to provide details of where transportation and storage conditions are out with those detailed by the Purchaser as site conditions. The manufacturer take measures to ensure these do not affect the integrity of the system. |  | Select | within normal service conditions | outwith normal service conditions - see comments box for details
28 |  | Longer periods of standstill : | [5 empty] | Select | Purchaser to advise when periods of standstill or storage or transport which exceed 6 months are anticipated. |  | Select | No | Yes
29 | 17.1.5, 17.8.1 | Maximum relative humidity : |  |  |  |  | Select | % | Advise maximum relative humidity, at maximum ambient air temperature defined in this data sheet, for which the water mist system shall be rated. |  | Select | 100 | 95 | 90 | other
30 | 17.8.1 | Ingress protection : | [5 empty] | Select | Advise ingress protection value according to IEC 60034-5 for which system or components shall be rated. |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
31 | 17.12 | LV Motors : | [5 empty] | Select | To clarify if manufacturers standards is required or to adopt JIP33 IOGP S-703L for hazardous areas only. N/A for cylinder based systems |  | Select | manufacturer's standard | IOGP S-703L | not applicable
32 |  | Supply voltage : |  |  |  |  | Select | V | Advise supply voltage for which system shall be rated for. |  | Select | 380 | 400 | 415 | 440 | 480 | 660 | 690 | other
33 |  | Supply frequency : |  |  |  |  | Select | Hz | Advise supply frequency for which system shall be rated for, if applicable |  | Select | 50 | 60 | N/A
34 |  | Electric pump system start up : | [5 empty] | Select | Supplier to advise on system starting type. |  | Select | DOL (Direct on line) | star delta | invertor
35 |  | System earthing : | [5 empty] | Select | Advise method of earthing arrangement as described in IEC 60364 |  | Select | TN-S | IT | TN-C | TN-C-S | TT | other
36 |  | Electrical requirement start-up (electric pump) Amps : |  |  |  |  | Input Data | A | Supplier to confirm maximum electrical power (Amps) required for the water mist system (electric pump system only) for full system design (start up).
37 |  | Electrical requirement start-up (electric pump) : |  |  |  |  | Input Data | kW | Supplier to confirm maximum electrical power required for the water mist system (electric pump system only) for full system design (start up).
38 |  | Electrical requirement running (electric pump) : |  |  |  |  | Input Data | A | Supplier to confirm (maximum) electrical power (Amps) required for the water mist system (electric pump system only) for running conditions.
39 |  | Electrical requirement running (electric pump) : |  |  |  |  | Input Data | kW | Supplier to confirm (maximum) electrical power required for the water mist system (electric pump system only) for running conditions.
40 |  | Electrical requirement running (diesel pump) : | [5 empty] | Input Data | Supplier to advise on specification requirements for diesel pump system.
41 |  | Electrical requirement (cylinder system) Amps : |  |  |  |  | Input Data | A | Supplier to confirm electrical power required for the water mist system (cylinder based system only) for system actuation.
42 |  | Electrical requirement (cylinder system) Volts : |  |  |  |  | Input Data | V
43 | 17.12, 17.9 | Hazardous Area Classification : | [5 empty] | Input Data | Determine actual location of the primary water mist components (nozzles/section control valve/pump-cylinder unit) and then find the area classification from hazardous area classification drawing.
44 | 17.9 | Hazardous Area Certification : | [5 empty] | Select | Purchaser to confirm certification required for end user location. |  | Select | IEC 60079 (IECEx) | API 500 (NRTL) | API 14 FZ(NRTL) | other
45 | 17.9 | Hazardous Protection Method : | [5 empty] | Input Data | Supplier to clarify protection certification of equipment
46 |  | SIL Capability for the Assembly : | [5 empty] | Select | If SIL is required, SIL level shall be stated by the purchaser, for the supplier conformance. |  | Select | SIL 1 | SIL 2 | SIL3 | none
47 | 16.2.15, 5.1.2, 6.5.2, 8.3.2, 8.3.6.2, 8.3.7, 8.4.2 | Complies with NFPA 13, Standard for the Installation of Sprinkler Systems : |  |  |  |  | Select | Input Data | Where NFPA 13 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
48 | 10.1.2.3, 10.1.2.4 | Complies with NFPA 14, Standard for the Installation of Standpipe and Hose Systems : |  |  |  |  | Select | Input Data | Where NFPA 14 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
49 | 10.3.1.9.2, 6.9.1.1, 6.9.2.1, 6.9.3.1, 8.8.3.1.9, C.1.1 | Complies with NFPA 20, Standard for the Installation of Stationary Pumps for Fire Protection : |  |  |  |  | Select | Input Data | Where NFPA 20 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
50 | 10.3.1.9.1, 12.5.3.1 | Complies with NFPA 22, Standard for Water Tanks for Private Fire Protection : |  |  |  |  | Select | Input Data | Where NFPA 22 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
51 | 15.1.1, 8.6.5 | Complies with NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems, : |  |  |  |  | Select | Input Data | Where NFPA 25 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
52 | 4.2.1.1, 6.10.1.1, 6.9.2.1, 8.9.1.1 , 8.9.2.1 | Complies with NFPA 70, National Electrical Code® : |  |  |  |  | Select | Input Data | Where NFPA 70 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
53 | 10.3.2.3, 10.3.2.5.6, 14.2.4.2.6, 6.10.1.1, 6.10.2.1, 6.10.4.1, 8.9.1.2, 8.9.1.3, 8.9.2.1, 8.9.2.2, 8.9.3.1 | Complies with NFPA 72®, National Fire Alarm and Signaling Code : |  |  |  |  | Select | Input Data | Where NFPA 72 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
54 | 13.1.6 | Complies with NFPA 170, Standard for Fire Safety and Emergency Symbols, : |  |  |  |  | Select | Input Data | Where NFPA 170 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
55 | 10.3.2.8.1.4 | Complies with NFPA 220, Standard on Types of Building Construction : |  |  |  |  | Select | Input Data | Where NFPA 220 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
56 | 14.2.2.3.1, 6.3.4.2, 6.3.4.3, 6.3.6.1, 8.3.2 | Complies with ASME B31.1, Power Piping Code, or BS EN-13480-3, Metallic Industrial Piping Design and Calculation. : |  |  |  |  | Select | Input Data | Where these standards do not apply, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
57 | 6.2.2.2, 6.4.3.5, 8.5.6.1 | Complies with ASME Boiler and Pressure Vessel Code, Section VIII or U.S. Department of Transportation, 49 CFR, 171-190, 178.36-178.37, or other approved international standards. : |  |  |  |  | Select | Input Data | Where these standards do not apply, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
58 | 6.4.2.7, 6.4.3.3 | Complies with ANSI/ASME B1.20.1, Pipe Threads, General Purpose (Inch) : |  |  |  |  | Select | Input Data | Where ANSI/ASME B1.20.1 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
59 | 14.2.4.2.6, 6.10.1.1 | Complies with CAN/ULC S524-14, Standard for the Installation of Fire Alarm Systems (in Canada) : |  |  |  |  | Select | Input Data | Where CAN/ULC S524-14, is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
60 | 14.2.4.2.6, 6.10.1.1 | Complies with CAN/ULC S529-16, Standard for Smoke Detectors for Fire Alarm Systems (in Canada) : |  |  |  |  | Select | Input Data | Where CAN/ULC S529-16 is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
61 | 16.1.8 | Complies with U.S. Coast Guard Navigation and Vessel Inspection Circular (NVIC) 9-97 CH-1, Guide to Structural Fire Protection. : |  |  |  |  | Select | Input Data | Where USCG circular is not applied, local or international requirements that are different from the above mentioned standard are permitted, when accepted by the authority having jurisdiction. Please add details here |  | Select | Yes | No | not applicable
62 | 16.1.2.1, 16.1.2.2, 17.1, 17.1.3.1, 17.2.1, 17.2.3, 17.2.4, 5.1.1, 5.1.2, 5.1.3, 5.2.2, 6.1.1.1, 6.6.1, 7.2.4.2, 9.1.5 | Approved System : | [5 empty] | Select | Define if a listed solution or fire scenario engineered solution. |  | Select | listed solution | fire scenario engineered solution
63 | 17.1.3.1, 17.1.3.2, 17.2.1, 17.2.3, 17.2.3.2, 9.1.5 | Fire Scenario Engineered Solution: Fire Testing : | [5 empty] | Input Data | Could further fire testing be required, and expand details.
64 | 17.1.3.1, 17.1.3.2, 17.2.1 | Authority having Jurisdiction : | [5 empty] | Input Data | Purchaser to advise on AHJ for the approval of the water mist system
65 | 16.1.2.1, 16.1.2.2, 6.1.1.1, 6.6.1, 7.2.4.2 | System Approval Body/Organisation : | [5 empty] | Input Data | If a listed system, define the approval body eg IMO, FM approvals, UL, VDS,. For Fire Scenario engineered solution the 3rd party and the fire test laboratory.
66 |  | System Approval : Professional Engineer : | [5 empty] | Input Data | In certain countries a PE (professional engineer) shall be required for system approval - please clarify if required and details.
67 | 13.2.3, 8.1.2, 8.1.6.1, 9.1.3, 9.2.6.1 | System Design Responsibility : | [5 empty] | Input Data | Entity responsible for the design of the water mist system
68 |  | System Installation Responsibility : | [5 empty] | Input Data | Entity responsible for the installation and commissioning of the water mist system
69 | 7.5 | System Type (Pressure) : | [5 empty] | Select | Clarify if system required is single or twin fluid and low. intermediate or high pressure |  | Select | low pressure | intermediate Pressure | high pressure
70 | 11.1.1, 11.4.1.1, 12.1.3, 12.6.1, 7.5, 8.8.4.4 | System Type (Fluid) : | [5 empty] | Select | Clarify media system type. |  | Select | single fluid | twin fluid
71 |  | Water Mist system supply type : | [5 empty] | Select | Determine method for delivering water (mist) to the protected item/spaces. |  | Select | Cylinder based | electric pump | diesel pump | gas driven pump (pneumatic)
72 |  | Cylinder System Propellant : | [5 empty] | Select | Clarify the media (pressurized gas) used to act as a a propellant |  | Select | Nitrogen | Air | other
73 | 11.4.1.3.2 | Full Discharge Test : | [5 empty] | Select | Clarify if full system discharge test is to performed. |  | Select | yes | no
74 | 5.2.2, 7.2 | Water Mist System Type : | [5 empty] | Select | Confirm water mist system type. (Note there may be more than one type on a project) |  | Select | deluge | dry pipe | engineered | fire scenario engineered | local-application | occupancy protection | preaction protection | total compartment | Zoned application
75 | 4.1.1.1 | Water Mist Performance Objective : | [5 empty] | Select | Define performance objective of the system. |  | Select | fire extinguishment | fire suppression | fire control | temperature control, exposure protection
76 |  | Protected item / area / volume : | [5 empty] | Input Data | confirm what is to be protected by water mist : Room/Enclosure/object and area/volume with dimensions
77 |  | Protected item / area (Additional fire protection) : | [5 empty] | Input Data | Identify if additional protection by other active fire suppression systems are providing protection (e.g. sprinklers, fixed gas extinguisher system).
78 |  | Protected Item / Area Storage : | [5 empty] | Input Data | Identify if the protected area has storage. Giving details of the materials, including any packaging, to be stored and the size of the room and contents.
79 |  | System Actuation : | [5 empty] | Select | to confirm how the system will operate, if the method is not in drop down, please describe. |  | Select | heat | flame | smoke | manual | other
80 | 8.2.2 | Maximum height of Protected item / area / volume : |  |  |  |  | Input Data | m | Confirm the maximum height of the protected item or space
81 | 17.1.5, 6.6.6.1 | Nozzle Protection : | [5 empty] | Select | To clarify if Frangible Discs and Blowoff Caps are required to avoid clogging by external, foreign materials |  | Select | frangible discs and blowoff caps | none
82 | 12.3.1 | Duration : Rundown time of turbine : |  |  |  |  | Input Data | mins | Purchaser to clarify the run down time of the turbine, if applicable.
83 | 12.3.1 | Duration : Time necessary to secure fuel lines to the rotating equipment : |  |  |  |  | Input Data | mins | Purchaser to clarify the time necessary to secure fuel lines to the rotating equipment, if applicable.
84 | 10.3.2.8.1.4, 16.3.9.1, 17.1.4.3, 6.10.3.7, 9.1.4, 9.2.3.2, 9.4.1, 9.4.1.2, 9.4.1.2.2.1, 9.4.1.2.2.2, FIGURE 8.2.10.2 | Ventilation : | [5 empty] | Input Data | Provide details of ventilation systems (including smoke ventilation) present in water mist protected rooms or compartments.
85 | 17.1.4.3, 9.4.1.2.1.1 , 9.4.1.2.1.2 | Ventilation : natural : | [5 empty] | Input Data | Provide details of doors, windows, shutters, other openings, and controls upon their use.
86 | 17.1.4.3 | Ventilation : forced : | [5 empty] | Input Data | Provide details of doors, windows, shutters, other openings, and controls upon their use.
87 |  | Process Equipment or Machinery : | [5 empty] | Input Data | Describe any interlocks provided to enable the water mist system to perform optimally. (e.g. fuel supply, power to equipment, process fluids).
88 |  | Details of Protected Areas/Objects : | [5 empty] | Input Data | Purchaser to supply detailed general arrangement drawings of the areas/objects to be protected by water mist.
89 | 8.6.1 | System Flow Rate (AMAO) : |  |  |  |  | Input Data | l/min | System flow rate for the AMAO (assumed maximum area of operation) or section(s) that requires the greatest demand.
90 |  | System Flow Rate (maximum number of nozzles) : | [5 empty] | Input Data | Record the maximum number of nozzles that will discharge water during operation in the event of a fire.
91 | 6.1.2.1, 6.2.2.4, 8.5.6.2 | System Pressure (Nozzle) : | [5 empty] | Input Data | Working pressure (most remote/demanding) nozzle. minimum or max/min range.
92 | 6.1.2.1, 6.2.2.4, 8.5.6.2 | System Pressure (Pump/cylinder) : |  |  |  |  | Input Data | bar | Operating pressure range for the pump/cylinder system.
93 |  | System Weight (dry) : |  |  |  |  | Input Data | kg | clarify the dry weight if the system (pump or cylinder system)
94 |  | System Weight (filled) : |  |  |  |  | Input Data | kg | clarify the filled weight of the system (pump or cylinder system)
95 | 6.10.3.4, 6.2.2.4 | Design Temperature range : |  | Input Data | °C | to | Input Data | °C | Clarify max / min design temperature of water mist system. (If heating and cooling is to be installed, this shall be considered and noted)
96 |  | Electric Motors (pump) : | [5 empty] | Select | To confirm that the manufactures motors are either standard or for hazardous areas. |  | Select | manufactures standard | hazardous area
97 | 16.1.6, 17.1.6 | Pump Redundancy : | [5 empty] | Select | To clarify that pump redundancy is required, and amount of redundancy. |  | Select | 0 | 1 | 2 | other
98 | 6.2.2.2, 8.5.5.1 | Gas and Water Containers (pressurized): approved international standard : | [5 empty] | Input Data | Confirm that pressurized Gas and Water Containers in accordance to which approved international standard.
99 | 6.2.2.2, 8.5.5.1 | Gas and Water Containers (pressurized): size. : |  |  |  |  | Input Data | l | Confirm pressurized Gas and Water Container size.
100 | 6.2.2.3 | Gas and Water Containers (shipping): approved international standard : | [5 empty] | Input Data | Confirm that pressurized Gas and Water Containers in accordance to which approved international standard
101 | 6.2.2.3 | Gas and Water Containers (shipping): size : |  |  |  |  | Input Data | l | Confirm pressurized Gas and Water Containers size.
102 | 17.1.7 | Cylinder Redundancy : | [5 empty] | Select | To clarify that cylinder redundancy is required, and what quantity |  | Select | 0 | 2 | 1 | other
103 |  | Nozzle characteristics (type 1): type/model : | [5 empty] | Input Data | Clarify nozzle type and model
104 |  | Nozzle characteristics (type 1): operating pressure : |  |  |  |  | Input Data | bar | Clarify nozzle operating pressure
105 |  | Nozzle characteristics (type 1): flow rate (as working pressure) : |  |  |  |  | Input Data | l/min | Clarify nozzle flow rate (at working pressure)
106 |  | Nozzle Materials : | [5 empty] | Input Data | Clarify material details of components within the nozzle.
107 | 8.2.2 | Nozzle Installation (Height) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters maximum permitted height from floor
108 | 8.2.6 | Nozzle Installation (Below Ceiling) : |  | Input Data | m (min) | to | Input Data | m (max) | Clarify nozzle installation parameters : maximum/minimum distance below the ceiling
109 | 8.2.3 | Nozzle Installation (Spacing) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters : maximum permitted spacing between nozzles.
110 | 8.2.4 | Nozzle Installation (Distance to wall) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters : maximum distance to wall / bulkhead
111 |  | Nozzle Installation (Distance above hazardl) : |  | Input Data | m (max) | to | Input Data | m (min) | Clarify nozzle installation parameters : maximum/minimum distance above hazard
112 | 8.2.5 | Nozzle Installation (Distance from obstruction) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters : minimum distance from obstruction
113 |  | Nozzle Installation (Orientation) : | [5 empty] | Select | Clarify nozzle installation parameters : (orientation) |  | Select | vertical | horizontal | angled
114 | 10.1.2.1.1, 12.3.1 | Duration (Discharge Time) : |  |  |  |  | Input Data | mins | To clarify the discharge time (duration) for the listed or fire scenario engineered solution
115 |  | Water Supply Tank : |  |  |  |  | Input Data | l | Clarify the main water tank (pumped systems only) size
116 |  | Water Supply Tank: spray time : |  |  |  |  | Input Data | mins | Clarify the main water tank (pumped systems only) spray time
117 |  | Deviation Requests : |  |  |  |  | Select | Input Data | Supplier to confirm if there are deviations, and provide details. |  | Select | Yes | No
118 | 8.5.4 | Fire Fighting Skid Enclosure Type : | [5 empty] | Input Data | Define what type of protective enclosure is require, e.g. blast protected, offshore, open, heated, vented, etc
119 |  | Enclosure : Material : | [5 empty] | Select | Clarify material for the enclosure (if required) where excessive climatic or mechanical exposures are expected, |  | Select | carbon steel | AISI 316L | not required
120 | 17.11 | Enclosure : Paint : | [5 empty] | Select | Clarify Enclosure paint process and colour (if required) - |  | Select | manufacturer's standard | JIP33 supplementary specification for painting and coating (S-715)
121 | 6.10.3.4, 8.5.6.6.2 | Enclosure : Heating / Cooling : | [5 empty] | Select | Clarify if cooling or heating is required for the enclosure (FFS) |  | Select | heating | cooling (forced) | cooling (naturally)
122 | 17.7.1.4 | Enclosure : Lighting : | [5 empty] | Select | Confirm if emergency lighting is required inside the FFS enclosure |  | Select | Yes | No
123 |  | Enclosure : Water Fill : | [5 empty] | Select | Purchaser to confirm if water filling is required (manual hand pump to refill water cylinders) |  | Select | Yes | No
124 | 6.10.3.5.1 | Enclosure : Emergency Release : | [5 empty] | Select | to clarify if a manual emergency release is required on the FFS enclosure |  | Select | Yes | No
125 | 17.5.2 | Water Supply : | [5 empty] | Select | To clarify where water for system replenishment comes from. |  | Select | processing plant mains | stored water | stored water relying on infill | other
126 |  | Water Supply (Additional connections) : | [5 empty] | Input Data | Identify all water supply connections, for fire protection or other purposes, which may draw water from the supply.
127 | 17.5.1 | Water (Quantity) : |  |  |  |  | Input Data | l | supplier to confirm designed quantity of water and duration/spray time.
128 |  | Water (Duration) : |  |  |  |  | Input Data | mins | supplier to confirm designed quantity of water and duration/spray time.
129 | 12.5.1.1, 12.5.1.7, 17.5 | Water (Quality): primary : | [5 empty] | Select | To confirm primary water supply types. |  | Select | potable | seawater | demineralized | filtered
130 | 12.5.1.1, 12.5.1.7, 17.5 | Water (Quality): backup : | [5 empty] | Select | To confirm backup water supply types. |  | Select | potable | seawater | demineralized | filtered | none | other
131 | 12.2, 6.2.2.6.1, 6.7.2, 7.6 | Water (Additives) : | [5 empty] | Select | Define any additives included in the water system |  | Select | enhanced fire performance | microbiologic growth inhibitors | corrosion inhibitors | freeze protection
132 | 6.10.3.4 | Water Supply (Freezing protection) : | [5 empty] | Input Data | Are freezing conditions ever likely to occur and what is the mitigation?
133 | 7.4.1.1, 8.8.1.8.2, 8.8.2.1, 8.8.2.2 | Section Control Valve : | [5 empty] | Select | To specify / clarify the type of section control valve (NO - normally open for wet pipe system ) (NC - normally closed for dry pipe system - electrical actuation) |  | Select | NO (hydraulic - wet pipe system) | NC (electrical - dry pipe system)
134 | 16.1.3.2 | Tubing and Fittings : | [5 empty] | Select | To clarify if manufacturers standards is required or to adopt JIP33 Supplementary Specification for instrument tubing and fittings (S-716) |  | Select | manufacturer's standard | JIP33 Supplementary specification for instrument tubing and fittings (S-716)
135 | 16.1.3.2, 17.10, 17.13, 6.3.1.1 | Material : | [5 empty] | Select | Supplier to qualify the piping/tubing to be used for this project. (Manufacturer's standard or JIP33 Supplementary Specification for instrument tubing and fittings (S-716) ) |  | Select | manufacturer's standard | JIP33 Supplementary specification for instrument tubing and fittings (S-716)
136 | 17.13, 6.3.5.1 | Tubing and fittings manufacturer and type : | [5 empty] | Input Data | Supplier to advise on the manufacturer of the tubing and fittings within the water mist system
137 | 17.13 | Tubing and fittings : Sizes : | [5 empty] | Input Data | Supplier to advise on sizes used for the tubing and fittings within the water mist system
138 | 17.13, 6.4.2.7 | Tubing and fittings : Threads : | [5 empty] | Input Data | Supplier to advise on thread sizes and type used for the tubing and fittings within the water mist system.
139 | 17.14, 6.2.2.9 | Pressure Gauge : | [5 empty] | Input Data | Supplier to confirm make and series of pressure gauge to be used as standard on this water mist system.
140 | 17.14 | Pressure Switch : | [5 empty] | Input Data | Supplier to confirm make and series of pressure switch to be used as standard on this water mist system.
141 | 17.14 | Pressure Transmitter : | [5 empty] | Input Data | Supplier to confirm make and series of pressure transmitter (if available) to be used as standard on this water mist system.
142 | 17.14 | Flow Indicator : | [5 empty] | Input Data | Supplier to confirm make and series of flow indicator (switch/meter) to be used as standard on this water mist system
143 | 17.14 | Water Level Indicator : | [5 empty] | Input Data | Supplier to confirm make and series of water level indicator to be used as standard on this water mist system.
144 | 17.14 | Valve Position Indicator : | [5 empty] | Input Data | Supplier to confirm make and series of valve position indicator to be used as standard on this water mist system.
145 | 14.2.6.1, 14.2.6.2, 14.2.6.3 | Full Discharge Test : | [5 empty] | Select | if full discharge test is required, at FAT (suppliers) or SAT (clients) |  | Select | FAT | SAT | not applicable
146 | 16.1.8, 17.1.9 | Pipe Penetrations : | [5 empty] | Input Data | To clarify pipe penetrations (see 17.1.9)
147 |  | Nozzle Characteristics (type 2): type/model : | [5 empty] | Input Data | Clarify nozzle type/model
148 |  | Nozzle Characteristics (type 2): operating pressure : |  |  |  |  | Input Data | bar | Clarify nozzle details for operating pressure
149 |  | Nozzle Characteristics (type 2): flow rate (at working pressure) : |  |  |  |  | Input Data | l/min | Clarify nozzle details of flow rate (at working pressure)
150 |  | Nozzle Materials : | [5 empty] | Input Data | Clarify material details of components within the nozzle.
151 |  | Nozzle Installation (Height) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters maximum permitted height from floor
152 |  | Nozzle Installation (Below ceiling) : |  | Input Data | m (max) | to | Input Data | m (min) | Clarify nozzle installation parameters : maximum/minimum distance below the ceiling
153 |  | Nozzle Installation (Spacing) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters : maximum permitted spacing between nozzles.
154 |  | Nozzle Installation (Distance to wall) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters : maximum distance to wall / bulkhead
155 |  | Nozzle Installation (Distance above hazard) : |  | Input Data | m (max) | to | Input Data | m (min) | Clarify nozzle installation parameters : maximum/minimum distance above hazard
156 |  | Nozzle Installation (Distance from obstruction) : |  |  |  |  | Input Data | m | Clarify nozzle installation parameters : minimum distance from obstruction
157 |  | Nozzle Installation (Orientation) : | [5 empty] | Select | Clarify nozzle installation parameters : (orientation) |  | Select | vertical | horizontal | angled
| DOCUMENT NUMBER : Insert Project Document Number |  | REV : Insert Project Document Revision
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Supplement
Row | S-719D Data Sheet for Water Mist Fire Protection |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
Public Review Draft

## Backcover
Public Review Draft