## Front & Preliminaries
|  |  |  | SPECIFICATION | June
|  |  |  | S-704D | 2020
Data Sheet for
High Voltage Three Phase
Cage Induction Motors
Revision history
| VERSION | DATE | PURPOSE
| 0.1 | June 2020 | Issued for Public Review
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
This publication is made available for information purposes and solely for the private
use of the user. IOGP will not directly or indirectly endorse, approve or accredit the
content of any course, event or otherwise where this publication will be reproduced.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
Data Sheet for
High Voltage Three Phase Cage Induction Motors
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2014).
Data Sheet for
High Voltage Three Phase Cage Induction Motors
Introduction
The purpose of this equipment data sheet is to define buyer specific requirements for the procurement of high voltage three phase cage induction motors, in accordance with IOGP S-704, for application in the petroleum and natural gas industries. The data sheet provides project specific requirements where the supplementary specification and its parent standard require the purchaser to define an application specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser supplied documents are also listed in the data sheets, to define scope and technical requirements for enquiry and purchase of the equipment.
This data sheet shall be used in conjunction with the supplementary requirements specification IOGP S-704, information requirements specification IOGP S-704L and quality requirements specification IOGP S-704Q which together comprise the full set of specification documents. The Introduction section in the supplementary requirements specification provides further information on the purpose of each of these documents and the order of precedence for their use.
JIP33 Specification for Procurement Documents Data Sheet
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Single-speed
Row |  | S-704D Data Sheet for High Voltage Three Phase Cage Induction Motors Single-speed Motor |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Model number : | Input Data
7 |  | Serial number : | Input Data
8 |  | Order status : | Select |  |  |  | Select | for enquiry | for purchase | as-build
9 |  | Conformity Assessment System (CAS) level : | D |  |  |  | Select | A | B | C | D
10 | 11.3.1.2 | Frame size : | Input Data
11 |  | Duty
12 | 4.1 | Duty type : | S1 |  |  |  | Select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10
13 |  | Number of poles : | Select |  |  |  | Select | 2 pole | 4 pole | 6 pole | 8 pole | other
14 | 5.5.3 | Duty point shaft power : | Input Data | kW
15 |  | Direction of rotation : | Select |  |  |  | Select | clockwise | counter-clockwise
16 |  | Load drive : | Select |  |  |  | Select | direct | belt | gearbox | other
17 | 9.13.1 | Pulsating torque requirement : | Select |  |  |  | Select | not require | required
18 | 11.3.7.4.3, 11.3.7.4.4 | External radial loading on the motor shaft end : | Input Data | N
19 | 11.3.7.4.3, 11.3.7.4.4 | External axial loading on the motor shaft end : | Input Data | N
20 |  | Moment of inertia of the load (Jext) : | Input Data | kg·m²
21 |  | Rating
22 | 11.11.2, 5.5.3 | Rated power output : | Input Data | kW
23 |  | Full load current (FLC) : | Input Data | A
24 |  | Site conditions
25 | 11.3.5.12 | Location environment : | Select |  |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship) | interior location
26 | 6.2 | Altitude : | 1000 | m |  |  | Select | 1000 | other
27 | 6.3 | Maximum ambient air temperature : | 40 | °C |  |  | Select | 40 | 45 | 50 | other
28 | 6.4, 6.6 | Minimum ambient air temperature : | -15 | °C |  |  | Select | -15 | -20 | -40 | other
29 | 6.6 | Transport and storage conditions : | within defined site conditions |  |  |  | Select | within defined site conditions | outside defined site service conditions - see comments box for details
30 | 6.6 | Standstill period : | ≤ 6 months |  |  |  | Select | ≤ 6 months | ≤ 9 months | ≤ 12 months | other
31 |  | Maximum relative humidity : | 100 | % |  |  | Select | 100 | 95 | 90 | other
32 | 6.8.1, 6.8.2 | Motor enclosure ingress protection : | Select |  |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
33 | 6.9 | Impact protection : | IK08 |  |  |  | Select | IK08 | IK09 | IK10
34 |  | Electrical operating conditions
35 |  | Motor rated voltage : | Input Data | kV
36 |  | Motor rated frequency : | Select | Hz |  |  | Select | 50 | 60
37 | 7.3, Figure 12 | Maximum operating voltage limit : | Select | % |  |  | Select | 10 | 6 | other
38 | 7.3, Figure 12 | Minimum operating voltage limit : | Select | % |  |  | Select | -10 | other
39 | 7.3, Figure 12 | Maximum operating frequency limit : | Select | % |  |  | Select | 3 | 5 | other
40 | 7.3, Figure 12 | Minimum operating frequency limit : | Select | % |  |  | Select | -5 | other
41 | 7.2.1.1, 7.1 | Power supply quality : | as per IEC 60034-1 section 7.2.1 |  |  |  | Select | as per IEC 60034-1 section 7.2.1 | class 1 as per 61000-2-4 | class 2 as per 61000-2-4 | class 3 as per 61000-2-4
42 |  | Rated thermal short circuit current : | Select |  |  |  | Select | 25 | 31.5 | 40 | other
43 |  | Rated peak withstand current : | Input Data | kA peak
44 |  | Stator connection : | Select |  |  |  | Select | star | delta
45 |  | Thermal performance
46 | 8.1 | Thermal class : | F |  |  |  | Select | F | H
47 | 8.1 | Temperature rise class : | B |  |  |  | Select | B | F
48 |  | Starting performance
49 |  | Starting method : | Select |  |  |  | Select | direct on line | star-delta | soft-starter | captive transformer | auto-transformer starter | other
50 | 9.5 | Pull-up torque : | Input Data | pu of FLT
51 | 9.12.1.1 | Declared locked rotor current tolerance : | 20 | % |  |  | Select | 20 | 10 | 0
52 |  | Starting current requirement : | Select |  |  |  | Select | As per S-704 9.12.1.1 | 4 x rated current | 5 x rated current | 6 x rated current
53 |  | Declared locked-rotor current at 100% rated voltage : | Input Data | pu of FLC
54 |  | Declared locked-rotor current at 80% rated voltage : | Input Data | pu of FLC
55 |  | Declared locked-rotor torque at 100% rated voltage : | Input Data | N·m
56 |  | Declared locked-rotor torque at 80% rated voltage : | Input Data | N·m
57 |  | Declared locked-rotor power factor at 100% rated voltage : | Input Data
58 |  | Moment of inertia of the motor (Jm) : | Input Data | kg·m²
59 |  | Locked-rotor withstand time (hot/cold) at 100 % rated voltage : | Input Data | s
60 |  | Locked-rotor withstand time (hot/cold) at 80 % rated voltage : | Input Data | s
61 |  | Operating performance
62 |  | Rated full load speed : | Input Data | r/min
63 |  | Rated full load torque : | Input Data | N·m
64 |  | Rated breakdown torque : | Input Data | pu of FLT
65 |  | Voltage at minimum continuous operating speed : | Input Data | V
66 |  | Voltage at maximum continuous operating speed at maximum torque : | Input Data | V
67 |  | Current at maximum continuous operating speed : | Input Data | A
68 |  | Current at minimum continuous operating speed : | Input Data | A
69 |  | Current at maximum continuous operating speed at maximum torque : | Input Data | A
70 | 9.15.1, Table 22 | Efficiency at 100% rated output : | Input Data | %
71 |  | Efficiency at 75% rated output : | Input Data | %
72 |  | Efficiency at 50% rated output : | Input Data | %
73 |  | Power factor at 100% rated output : | Input Data | pu
74 |  | Power factor at 75% rated output : | Input Data | pu
75 |  | Power factor at 50% rated output : | Input Data | pu
76 |  | Special testing as per S-704 Table 16C
77 | Table 16C | Noise level test at no load : | not required |  |  |  | Select | not required | required | report from identical motor previous test accepted
78 | Table 16C | Measurement of moment of inertia : | not required |  |  |  | Select | not required | required
79 | Table 16C | Measurement of torque and current as a function of speed test : | not required |  |  |  | Select | not required | required
80 | Table 16C | Measurement of axial shaft displacement : | not required |  |  |  | Select | not required | required
81 | Table 16C | Dielectric dissipation test (tan δ) on stator windings : | not required |  |  |  | Select | not required | required
82 | Table 16C | Partial discharge test on complete stator : | not required |  |  |  | Select | not required | required
83 | Table 16C | Sealed winding conformance test : | not required |  |  |  | Select | not required | required
84 | Table 16C | Unbalanced response test : | not required |  |  |  | Select | not required | required
85 | Table 16C | Bearing housing natural frequency test : | not required |  |  |  | Select | not required | required
86 | Table 16C | Impulse voltage withstand tests of sample coils : | not required |  |  |  | Select | not required | required
87 | 7.5, Table 16C | Dielectric dissipation tests (tan δ) of sample coils : | not required |  |  |  | Select | not required | required
88 | Table 16C | Partial discharge test of sample coils : | not required |  |  |  | Select | not required | required
89 |  | Noise
90 | 9.16.1, 9.16.2, Table 16C | Maximum permissible noise limit : | Input Data | db(A)
91 | 9.16.1, 9.16.2 | Maximum declared motor sound power level at no-load : | Input Data | db(A)
92 | 9.16.1, 9.16.2 | Maximum expected motor sound power level at full load : | Input Data | db(A)
93 |  | Machine construction
94 |  | Motor weight : | Input Data | kg
95 |  | Rotor
96 |  | Rotor weight : | Input Data
97 |  | Terminal box(es)
98 |  | General
99 | 6.8.1 | Ingress protection of all terminal box(es) : | IP55 |  |  |  | Select | IP55 | IP56 | other
100 | 6.8.1 | Confirmation of ingress protection of all terminal box(es) : | Input Data
101 |  | Line conductor terminal box
102 |  | Line conductor terminal box type : | manufacturers standard |  |  |  | Select | manufacturers standard | air insulated | phase insulated with heat shrink insulation | phase insulated with separable connectors | phase separated | phase segregated
103 |  | Line conductor terminal box location : | Select |  |  |  | Select | R | B | L | T
104 |  | Line conductor terminal box cable entries : | Input Data
105 | 11.3.5.4 | Line conductor specification : | Input Data | mm²
106 | 11.7.3, 11.7.4 | Surge protection : | not required |  |  |  | Select | not required | required,
107 | 11.3.5.13 | Portable earth connection point : | Select |  |  |  | Select | Manufacturer's standard | none | 20 mm ball connection | 25 mm ball connection
108 |  | Star point terminal box
109 | 11.3.5.8, 11.8.1 | Star point terminal box required : | Select
110 |  | Space heater terminal box
111 | 11.3.5.15, 11.3.8.3 | Space heater terminal box cable entries : | Select |  |  |  | Select | M20 | M25
112 |  | Space heater supply cable cross-section area : | Select | mm² |  |  | Select | 2.5 | 4 | 6
113 |  | Auxiliary terminal box(es)
114 | 11.3.5.15 | Winding temperature detection terminal box cable entries : | Input Data
115 | 11.3.5.15 | Bearing temperature detection terminal box cable entries : | Input Data
116 | 11.3.5.15 | Vibration detection terminal box cable entries : | Input Data
117 |  | Differential protection
118 | 11.8.1, 11.8.5.9 | Differential protection : | Select |  |  |  | Select | not required | required
119 |  | Bearings (general)
120 | 11.3.7.1.1, 11.3.7.1.2 | Required bearing type : | Select |  |  |  | Select | As per S-704 | sleeve bearings | rolling element bearings
121 | 11.3.7.1.1, 11.3.7.1.2 | D-end bearing type : | Input Data
122 | 11.3.7.1.1, 11.3.7.1.2 | N-end bearing type : | Input Data
123 | 11.3.7.4.1, 11.3.7.4.10 | Lubrication specification : | Input Data
124 | 11.3.7.2.2 | D-end insulated bearing : | Select |  |  |  | Select | not required | required
125 | 11.3.7.1.2 | Driven equipment bearing type : | Select |  |  |  | Select | sleeve bearings | rolling element bearings | unknown
126 | 11.3.7.2.2 | Insulated coupling : | Select |  |  |  | Select | non-insulated coupling | insulated coupling | unknown
127 |  | Sleeve bearings
128 | 9.1.2.2 | Minimum lube oil temperature : | Input Data | °C
129 | 11.3.7.3.9, 9.1.2.2 | Maximum lube oil temperature : | Input Data | °C
130 | 9.1.2.2 | Minimum lube oil pressure : | Input Data
131 | 9.1.2.2 | Maximum lube oil pressure : | Input Data
132 |  | Rolling element bearings
133 |  | Internal clearance : | Select |  |  |  | Select | C3 | C2 | CN | C4 | C5
134 | 11.3.7.4.5, 11.3.7.4.6, 11.3.7.4.7 | Vibration monitoring : | Select |  |  |  | Select | none | SPM nipples
135 | 11.3.7.4.5 | Shock pulse monitoring connection : | Input Data
136 | 11.3.7.4.1 | Relubrication interval : | Input Data | hours
137 |  | Lubrication plate : | Input Data |  |  |  | Select | not required | required
138 |  | Space heaters
139 | 11.3.8.1, 11.3.8.2 | Heater requirement : | required |  |  |  | Select | required | not required
140 | 11.3.8.1 | Supply voltage : | Select | V |  |  | Select | 100-120 | 200-240
141 | 11.3.8.4 | Warning label language : | Select |  |  |  | Select | English | other - see comment
142 |  | Mounting
143 | 11.4.1, Table 23 | Mounting arrangement : | Select |  |  |  | Select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | IM V1 (IM 3015) | IM V6 (IM 1035) | IM B3 (IM 1003) | other
144 |  | Cooling
145 | 11.5.1, Table 24 | Cooling method : | Select |  |  |  | Select | IC4A1A1 | IC5A1A1 | IC6A1A1 | IC8A1W7 | other
146 |  | Air to water heat exchanger
147 | Table 16A, Table 16B | Heat exchanger design code : | Select |  |  |  | Select | EN 13445 | ASME B31.3 | other
148 | 11.5.4.7, 11.5.4.8 | Cooling water specification : | Select |  |  |  | Select | fresh water | salt water
149 | 11.5.4.7, 11.5.4.8 | System material specification : | Input Data
150 | 9.1.2.1 | Maximum cooling water inlet temperature : | Input Data | ° C
151 | 9.1.2.1 | Maximum cooling water inlet pressure : | Input Data | bar
152 | 9.1.2.1 | Minimum cooling water inlet pressure : | Input Data | bar
153 | 9.1.2.1 | Maximum cooling water flow rate : | Input Data | l/s
154 | 9.1.2.1 | Minimum cooling water flow rate : | Input Data | l/s
155 |  | Vibration
156 | 9.1.2.2, 9.1.2.9 | Bearing housing vibration limits : | Select |  |  |  | Select | grade A | grade B | API 541 | other
157 | 11.3.3.3, 11.3.3.4, 9.1.2.2, 9.1.2.6, 9.1.2.7, 9.1.2.8, 9.1.2.9 | Shaft displacement vibration limits : | Select |  |  |  | Select | grade A | grade B | API 541 | other | NA
158 | 11.3.3.3, 11.3.3.4, 9.1.2.2, 9.1.2.6, 9.1.2.7, 9.1.2.8, 9.1.2.9 | Shaft displacement runout limits : | Select |  |  |  | Select | grade A | grade B | API 541 | other | NA
159 | 9.14.1, 9.14.2 | First critical speed : | Input Data | rpm
160 | 11.12 | Lateral vibration analysis : | Select |  |  |  | Select | not required | required
161 | 11.13.1, 11.13.2 | Torsional vibration analysis : | Select |  |  |  | Select | not required | required
162 |  | Surface protection
163 | 11.3.1.6, 11.3.1.7, 11.3.1.8, 11.3.4.1, 11.5.5, 11.6.1, 11.6.2 | Surface protection corrosivity category : | Select |  |  |  | Select | C3 | C4 | C5 | CX
164 | 11.6.3 | Surface protection durability category : | medium (M) 7 to 15 years |  |  |  | Select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
165 |  | Surface finish : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Norsok M-501 system no.1 | Norsok M-501 system no. 2A | Norsok M-501 system no. 2B
166 |  | Paint colour : | manufacturer's standard |  |  |  | Select | manufacturer's standard | other
167 |  | Temperature monitoring
168 | 11.7.1 | Winding temperature monitoring : | Select |  |  |  | Select | 2 x 3-wire | 3 x 4-wire
169 | 11.3.7.1.3 | Bearing temperature monitoring : | 1 x 3-wire | Pt-100 per bearing |  |  | Select | 1 x 3-wire | 1 x 4 wire | 2 x 3-wire | 2 x 4-wire
170 |  | Winding partial discharge monitoring
171 | 11.3.5.7 | On-line winding partial discharge measurement : | Select |  |  |  | Select | none | capacitive method | inductive method
172 |  | Converter-fed motor data
173 |  | Motors intended for use in potentially explosive atmospheres
174 | 15.1.1 | Explosion protected motor : | Select |  |  |  | Select | no | yes
175 | 15.1.2 | Hazardous area equipment certifying body : | Select |  |  |  | Select | ATEX | IECEx | EAC | CCC Ex | other
176 | 15.1.3 | Temperature group : | T3 |  |  |  | Select | T3 | T4 | T5 | T6 | T1 | T2
177 | 15.1.3 | Gas group : | IIB |  |  |  | Select | IIB | IIA | IIC
178 | 15.1.2, 15.1.5 | Equipment protection level : | Select |  |  |  | Select | EPL Ga | EPL Gb | EPL Gc | other
179 | 15.1.4, 15.3.1, Table 25 | Classification : | Select |  |  |  | Select | Ex db | Ex db eb | Ex eb | Ex ec | Ex pxb | Ex pyb | Ex pzc
180 | 15.5.1 | tE time at 100% voltage : | Input Data | s
181 |  | tE time at 80% voltage : | Input Data | s
182 |  | Miscellaneous
183 |  | Provision for IoT hardware installation : | Select |  |  |  | Select | required | not required
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C6: Input motor model number.
Note on C7: Input motor serial number.
Note on C8: Select order status.
Note on C9: Select CAS level as defined in S-704Q, Annex A. IOGP default is D. CAS level can be raised if more purchaser involvement is required.
Note on C10: Input motor frame size. IEC 60072 series defines preferred frame sizes for a.c. induction motors
Note on C12: Input the duty type as defined in IEC-60034-1 Section 4. IOGP default is S1 for single-speed use. For converter-fed motors, duty S9 or S10 may be applicable, or an S1 duty motor, depending on the load profile.
Note on C13: Select the required number of magnetic poles. For 10 poles and above, select 'other' and enter the required number of poles in the additional comments.
Note on C14: Input the driven load maximum duty power requirement. This value should include any sizing margin requirements.
Note on C15: Select the direction of motor shaft rotation observed when facing the D-end (motor drive end). Default motor direction of rotation is clockwise, when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C16: Select method of power transfer to driven equipment. Assists with selection of bearings which may be potentially subjected to higher axial or radial loading.
Note on C17: Pulsating torque requirement related to load characteristics such as reciprocating compressor or pump. The manufacturer will ensure the criteria stated in S-704 9.1.3 is met and motor will be subject to torsional analysis report.
Note on C18: Purchaser to input maximum anticipated radial loading on the shaft end for belt driven loads. Supplier to input maximum permissible radial loading if not defined by the Purchaser. Radial forces are those that are perpendicular to the motor shaft.
Note on C19: Purchaser to input maximum anticipated axial loading on the shaft end. Supplier to input maximum permissible axial loading if not defined by the Purchaser. Axial forces are those that are linear to (act along) the motor shaft.
Note on C20: Input the maximum moment of inertia of the load.
Note on C22: Input the motor shaft rated mechanical power output at the defined maximum ambient air temperature.
Note on C23: Confirm the motor full load current whilst operating at rated voltage and rated frequency.
Note on C25: Select location motor shall be situated as per the options available.
Note on C26: Altitude above sea-level. IEC 60034-1 default is 1000 m. Modify 1000 m value only if the site conditions are higher than the IEC default.
Note on C27: IEC 60034-1 default is 40 °C. Modify 40°C value only if the site conditions are higher than the IEC default. 40 °C aligns with the IEC 60079 series default maximum ambient air temperature requirement.
Note on C28: IEC 60034-1 default is -15°C. Modify -15°C value only if the site conditions are lower than the IEC 60034-1 default. -20°C aligns with the IEC 60079 series default minimum ambient air temperature requirement.
Note on C29: Manufacturer to provide details when special packing or controlled storage is required for the transportation and storage conditions detailed by the Purchaser
Note on C30: Purchaser to advise when periods of standstill or storage or transport which exceed 6 months are anticipated, as described in IEC 60034-1 Section 6.6.
Note on C31: IEC 60034-1 Section 6 does not address site humidity. Select the required maximum relative humidity at the maximum ambient air temperature defined in this data sheet.
Note on C32: Select the ingress protection value according to IEC 60034-5. IOGP default is IP55 for 'totally enclosed' motors. NOTE: For interior (indoor) locations, the requirement for a degree of ingress protection lower than IP55 can be evaluated by the user
Note on C33: ​Select the IK code for impact protection with regards to impact energy according to IEC 62262. IOGP default is IK08. This rating will include the motor enclosure and all auxiliary equipment. IEC 60034-1 does not address impact protection.
Note on C35: Purchaser to advise the input voltage, expressed as kV, for which the motor shall be rated.
Note on C36: Select the supply frequency for which the motor shall be rated.
Note on C37: Select the maximum steady-state voltage limit as a percentage of supply voltage. IEC 60034-1 Figure 12 zone B upper Y boundary default is 1.10 pu (+10%). IEC 61892-1 Table 1 defines +6% limit voltage for offshore 'island' networks.
Note on C38: Select the minimum steady-state voltage limit as a percentage of supply voltage. IEC 60034-1 Figure 12 zone B lower Y boundary default is 0.90 pu (-10%).
Note on C39: Select the maximum steady-state frequency limit as a percentage of supply frequency. IEC 60034-1 Figure 12 zone B upper X boundary default is 1.03 pu (+3%). IEC 61892-1 Table 1 defines +5% limit frequency for offshore 'island' networks.
Note on C40: Select the minimum steady-state frequency limit as a percentage of supply frequency. IEC 60034-1 Figure 12 zone B lower X boundary default is 0.95 pu (-5%).
Note on C41: For single-speed motors, select the total harmonic distortion in the electrical supply for which the motor shall be rated.
Note on C42: Confirm the rated short-time thermal withstand current with respect to 0.2 seconds for which the motor shall be rated.
Note on C43: Confirm the rated peak withstand current for which the motor shall be rated.
Note on C44: Confirm configuration of stator winding connection
Note on C46: Select the thermal class of the motor according to IEC 60085. IOGP default is class F.
Note on C47: Select the temperature rise class of motor according to IEC 60085. IOGP default is class B rise (for motors with class F insulation). For class H insulated motors (such as fire-water pump motors) the default is class F rise.
Note on C49: Select the motor starting method for which the motor will be provided.
Note on C50: Confirm the smallest steady-state asynchronous torque which the motor develops between zero speed and the speed which corresponds to the breakdown torque, when the motor is supplied at 100% rated voltage and rated frequency.
Note on C51: Confirm accepted tolerance for declared locked rotor current tolerance. Whilst the default is +20% as per IEC 60034-1 Table 21, it is acknowledged that some projects may require a more stringent value to be imposed.
Note on C52: Purchaser to advise where a project specific starting current value with zero positive tolerance is required. Expressed as a per unit value of full load current (Is/In)
Note on C53: Confirm as a per unit value of full load current (Is/In)
Note on C54: Confirm at 80% rated voltage and rated frequency, as a per unit value of full load current (Is/In).
Note on C55: Confirm the smallest measured torque the motor develops at its shaft and with the rotor locked, over all its angular positions, at rated voltage and frequency.
Note on C56: Confirm the smallest measured torque the motor develops at its shaft and with the rotor locked, over all its angular positions, at 80% rated voltage and rated frequency.
Note on C57: Confirm the power factor with the rotor locked, at rated voltage and frequency.
Note on C58: Confirm the motor moment of inertia as defined in IEC 60034-1 Clause 3.24.
Note on C59: Confirm the locked-rotor withstand time at 100 % rated voltage from hot and from cold (expressed as x/x s)
Note on C60: Confirm the locked-rotor withstand time at 80 % rated voltage from hot and from cold (expressed as x/x s)
Note on C62: Confirm the steady-state asynchronous rotor speed whilst delivering 100% rated power.at the rated voltage and frequency. Note: Includes the slip of the motor at full load and at working temperature.
Note on C63: Confirm the steady-state asynchronous rotor torque whilst delivering 100% rated power.at the rated voltage and frequency.
Note on C64: Confirm the maximum steady-state asynchronous torque which the motor develops without an abrupt drop in speed, when the motor is supplied at the rated voltage and frequency.
Note on C65: Confirm the voltage at motor terminals at minimum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C66: Confirm the voltage at motor terminals at maximum continuous operating speed at maximum torque as per IEC 61800-4.
Note on C67: Confirm the current at maximum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C68: Confirm the current at minimum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C69: Confirm the current at maximum continuous operating speed at maximum torque as per IEC 61800-4.
Note on C70: Confirm the efficiency of the motor whilst operating at 100% rated power.
Note on C71: Confirm the efficiency of the motor whilst operating at 75% rated power.
Note on C72: Confirm the efficiency of the motor whilst operating at 50% rated power.
Note on C73: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 100% rated power.
Note on C74: The cosine of the angle between active power and apparent power when the motor is operated at 75% rated power.
Note on C75: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 50% rated power.
Note on C77: Advise if a noise level test at no load is to be performed. IOGP default is set at 'not required'. Where an identical motor test report from a previous test can be provided, this will be included as an appendix to the test report.
Note on C78: Purchaser to advise if a measurement of moment of inertia test by retardation method is required. JIP33 default is set at 'not required'.
Note on C79: Measurement of torque and current as function of speed test from standstill to synchronous speed (for single-speed motors), results to be plotted and provided as a graph to the purchaser.
Note on C80: Test to be performed to measure axial shaft displacement.
Note on C81: Dielectric dissipation test (tan δ) for measurement of dielectric losses in stator winding insulation system. Testing to be performed in accordance with IEC 60894 and EN 50209.
Note on C82: Purchaser to advise when a partial discharge measurement on completed winding is required. See API 541 6.3.4.6 for guidance.
Note on C83: Purchaser to advise when a sealed winding conformance test is required. See NEMA MG 1 Part 20 for guidance.
Note on C84: Purchaser to advise when an unbalanced response test is required. See API 541 section 6.3.5.3.
Note on C85: Purchaser to advise when a bearing housing natural frequency test is required. See API 541 section 6.3.5.4.
Note on C86: Purchaser to advise when a sample coil impulse voltage withstand test on 2 sample coils is required.
Note on C87: Purchaser to advise when the dielectric dissipation tests (tan δ) of 2 sample coils is required
Note on C88: Purchaser to advise when partial discharge testing on 2 sample coils is required.
Note on C90: Input the maximum permissible motor A-weighted sound power level at full load including harmonic noise content. Where there is no maximum permissible sound power level state 'NA' in input data.
Note on C91: Confirm the manufacturer declared motor A-weighted sound power level at no-load. IEC 60034-9 Tables 1 and 2 stipulate maximum A-weighted sound power levels at no-load.
Note on C92: Confirm the manufacturer expected A-weighted sound power level, in dB(A) for rated load condition. IEC 60034-9 states that full load noise is not a measured value, but expressed as an expected increase added to the measured no-load value.
Note on C94: Confirm the fully assembled weight of the motor.
Note on C96: Confirm the weight of the rotor, this value is required to facilitate its installation and removal on-site.
Note on C99: Select the ingress protection method according to IEC 60034-5 for which all the terminal box(es) shall be rated.
Note on C100: Supplier to confirm ingress protection method according to IEC 60034-5 for which all the terminal box(es) are rated.
Note on C102: Confirm terminal box specification with regards to design and construction principals. Phase segregated and phase separated designs typically have the capability to eliminate phase to phase faults.
Note on C103: Confirm line conductor terminal box location using coding in accordance with IEC 60034-7
Note on C104: Confirm number, size and type of cable entries in main terminal box e.g. '1 x M32, 2 x M20 cable glands'. State 'un-drilled' where applicable. Where cable entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C105: Confirm line conductor cable size, type and number of cables. E.g. for multi-core cable 3 x 50, for singles 3 x 1 x 50, for multi-cores in parallel 2 x 3 x 50, for singles in parallel 6 x 1 x 50.
Note on C106: Surge protection devices may be installed in the terminal box in the form of surge arresters and surge capacitors to provide protection to the motor insulation from power surges, switching transients, faults and lightning strikes.
Note on C107: Where a fully insulated termination system is not provided confirm where the manufacturer is to provide a connection point on each phase and earth for the attachment of a portable earthing device.
Note on C109: Purchaser to confirm where a separate star point terminal box is required. This is typically used to located differential protection current transformers and to facilitate winding testing activities.
Note on C111: Confirm size of cable entry in main terminal box e.g. 'M20'. State 'un-drilled' where applicable. Where gland entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C112: Where known, purchaser to confirm cross-section area of line conductor to be terminated in the terminal box. Where line conductor cross-section area is not known, the supplier shall confirm maximum connectable cross-section area capacity of terminal box.
Note on C114: Confirm number and size of cable entries in winding temperature detection terminal box e.g. '1 x M25, 1 x M20'. State 'un-drilled' where applicable. Where entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C115: Confirm number and size of cable entries in bearing temperature detection terminal box e.g. '1 x M25, 1 x M20'. State 'un-drilled' where applicable. Where entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C116: Confirm number and size of cable entries in vibration detection terminal box e.g. '1 x M25, 1 x M20'. State 'un-drilled' where applicable. Where entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C118: Confirm requirement for pre-installed differential protection current transformers to be provided by the supplier.
Note on C120: Purchaser to confirm required bearing type where it differs from S-704 section 11.3.7.1.2. This may be to correspond with driven equipment bearing type or to accept manufacturer's standard offering where it has been assessed for use.
Note on C121: Confirm the D-end (drive end) bearing model number.
Note on C122: Confirm the N-end (non-drive end) bearing model number.
Note on C123: Confirm the approved lubrication type for the bearing. This will be the grease for rolling element bearings and oil for sleeve bearings.
Note on C124: Select 'required' where d-end bearing insulation is required.
Note on C125: Confirm driven equipment bearing type for consideration when selecting motor bearing type
Note on C126: Purchaser to advise manufacturer where it is known that an insulated coupling is provided, Where an insulated coupling is provided the a shaft grounding system on the N-end of the rotor shaft may be accepted.
Note on C128: Confirm minimum lube oil temperature for which the sleeve bearing is rated to operate.
Note on C129: Confirm maximum lube oil temperature for which the sleeve bearing is rated to operate.
Note on C130: Confirm minimum lube oil pressure for which the sleeve bearing is rated to operate.
Note on C131: Confirm maximum lube oil pressure for which the sleeve bearing is rated to operate.
Note on C133: Confirm the required internal clearance of bearing in accordance with ISO 5753-1 . C3 (group 3) refers to 'greater than normal' clearance as commonly used to avoid too little internal bearing clearance for high voltage motors.
Note on C134: Confirm if there is a requirement for a vibration monitoring connection point to be provided.
Note on C135: Where shock pulse monitoring connection points are to be provided, the purchaser shall confirm site connection type requirement.
Note on C136: Confirm the maximum recommended lubrication interval for where regreasable bearings have been provided. Where regreasing is not applicable input 'N/A' in data field
Note on C137: Confirm when a dedicated lubrication plate is to be attached to the motor stating bearing type, regreasing amount, regreasing intervals and grease product code.
Note on C139: IOGP default position is that space heaters shall be provided.
Note on C140: Input the supply voltage for which the heater shall be rated.
Note on C141: Confirm the language for which the label, warning that heater terminals may be live when the motor is isolated, should be written. Where the language is other than English, this can be confirmed in the 'additional comments' section
Note on C143: Confirm the motor mounting arrangement in accordance with IEC 60034-7.
Note on C145: Confirm the motor cooling method in accordance with IEC 60034-6.
Note on C147: Supplier to confirm design code which the heat exchanger has been manufactured and tested in accordance with.
Note on C148: Confirm specification of cooling water medium
Note on C149: Supplier to confirm system material specification. To be in accordance with S-704 section 11.5.4.
Note on C150: Input maximum cooling water inlet temperature as per project specification and site conditions.
Note on C151: Input maximum cooling water inlet pressure as per project specification and site conditions.
Note on C152: Input minimum cooling water inlet pressure as per project specification and site conditions.
Note on C153: Input maximum cooling inlet water pressure as per project specification and site conditions.
Note on C154: Input minimum cooling water flow rate as per project specification and site conditions.
Note on C156: Input the maximum Bearing housing vibration limits in IEC 60034-14 Table 1 or API 541
Note on C157: Input the maximum shaft displacement vibration limits in IEC 60034-14 Table 1 or API 541.
Note on C158: Input the maximum shaft displacement runout limits in IEC 60034-14 Table 1 or API 541.
Note on C159: Confirm the first speed at which the amplitudes of the vibrations of a machine rotor due to shaft torsional vibration reach their maximum values
Note on C160: Where lateral vibration analysis is required this will be carried out for both FAT (rigid workshop floor) and final site conditions (flexible skid or foundation) in accordance with API 541 clause 4.4.6.2.1.
Note on C161: Torsional vibration analysis will be performed in accordance with API 541 clause 4.4.6.2.2 and IEC 61800-4 clause 9.4.2
Note on C163: Advise surface corrosivity category in accordance with ISO 12944-2 Section 5.1.1.
Note on C164: Advise surface durability category in accordance with ISO 12944-1 Section 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme.
Note on C165: Advise surface finish requirements.
Note on C166: Where standard manufacturer paint colour is unacceptable, confirm specific paint colour requirements in 'additional comments'.
Note on C168: Confirm requirement for embedded temperature monitoring in the stator windings, Use comments section to confirm device transition set-point.
Note on C169: Where required select bearing temperature monitoring devices, these will be provided in pairs to facilitate d-end and n-end temperature monitoring. Use comments section to confirm device transition set-point.
Note on C171: Confirm whether on-line winding partial discharge measurement is required. Typical capacitive method is by coupling capacitors. Typical inductive method include is by rogowski coils. Where further detail is required use the comments field to advise.
Note on C174: Confirm whether the motor shall be rated for use in a potentially explosive atmosphere in accordance with IEC 60079
Note on C175: Confirm which certification or notified body shall be accepted for motors to be located in a hazardous area.
Note on C176: Confirm temperature group according to IEC 60079-0 for which machine shall be rated.
Note on C177: Confirm gas group according to IEC 60079-0 for which machine shall be rated.
Note on C178: Confirm equipment protection level (EPL) according to IEC 60079-14
Note on C179: Confirm classification according to IEC 60079 for which motor shall be rated.
Note on C180: time, in seconds, taken for an a.c. rotor or stator winding, when carrying the initial starting current IA, to be heated up to the limiting temperature from the temperature reached at 100% voltage at the maximum ambient temperature
Note on C181: time, in seconds, taken for an a.c. rotor or stator winding, when carrying the initial starting current IA, to be heated up to the limiting temperature from the temperature reached at 80% voltage at the maximum ambient temperature
Note on C183: Where the supplier offers IoT hardware which shall be attached to the motor, mounting points and all other provisions shall be made to facilitate this. Note: This may be to allow the IoT system to be procured at a later date.

## Converter-fed
Row |  | S-704D Data Sheet for High Voltage Three Phase Cage Induction Motors Converter-fed Motor |  |  |  | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  |  |  |  | Default
4 | Ref. Clause | Description |  |  | Additional notes
5 |  | General
6 |  | Manufacturer : | Input Data
7 |  | Model number : | Input Data
8 |  | Serial number : | Input Data
9 |  | Order status : | Select |  |  |  | Select | for enquiry | for purchase | as-build
10 |  | Conformity Assessment System (CAS) level : | D |  |  |  | Select | A | B | C | D
11 | 11.3.1.2 | Frame size : | Input Data
12 |  | Duty
13 | 4.1 | Duty type : | S1 |  |  |  | Select | S1 | S2 | S3 | S4 | S5 | S6 | S7 | S8 | S9 | S10
14 |  | Number of poles : | Select |  |  |  | Select | 2 pole | 4 pole | 6 pole | 8 pole | other
15 | 5.5.3 | Duty point shaft power : | Input Data | kW
16 |  | Direction of rotation : | Select |  |  |  | Select | clockwise | counter-clockwise
17 |  | Load drive : | Select |  |  |  | Select | direct | belt | gearbox | other
18 | 9.13.1 | Pulsating torque requirement : | Select |  |  |  | Select | not require | required
19 | 11.3.7.4.3, 11.3.7.4.4 | External radial loading on the motor shaft end : | Input Data | N
20 | 11.3.7.4.3, 11.3.7.4.4 | External axial loading on the motor shaft end : | Input Data | N
21 |  | Moment of inertia of the load (Jext) : | Input Data | kg·m²
22 |  | Rating
23 | 11.11.2, 5.5.3 | Rated power output : | Input Data | kW
24 |  | Full load current (FLC) : | Input Data | A
25 | 9.14.2 | Minimum operating speed : | Input Data | rpm
26 | 9.14.2 | Maximum operating speed : | Input Data | rpm
27 |  | Site conditions
28 | 11.3.5.12 | Location environment : | Select |  |  |  | Select | onshore – coastal | onshore – desert | onshore – inland | offshore – fixed | offshore – floating | marine (ship) | interior location
29 | 6.2 | Altitude : | 1000 | m |  |  | Select | 1000 | other
30 | 6.3 | Maximum ambient air temperature : | 40 | °C |  |  | Select | 40 | 45 | 50 | other
31 | 6.4, 6.6 | Minimum ambient air temperature : | -15 | °C |  |  | Select | -15 | -20 | -40 | other
32 | 6.6 | Transport and storage conditions : | within defined site conditions |  |  |  | Select | within defined site conditions | outside defined site service conditions - see comments box for details
33 | 6.6 | Standstill period : | ≤ 6 months |  |  |  | Select | ≤ 6 months | ≤ 9 months | ≤ 12 months | other
34 |  | Maximum relative humidity : | 100 | % |  |  | Select | 100 | 95 | 90 | other
35 | 6.8.1, 6.8.2 | Motor enclosure ingress protection : | Select |  |  |  | Select | IP55 | IP56 | IP54 | IP44 | IP23 | other
36 | 6.9 | Impact protection : | IK08 |  |  |  | Select | IK08 | IK09 | IK10
37 |  | Electrical operating conditions
38 |  | Motor rated voltage : | Input Data | kV
39 |  | Motor rated frequency : | Select | Hz |  |  | Select | 50 | 60
40 | 7.2.1.1 | Impulse voltage insulation class : | Select |  |  |  | Select | None | IVIC Class 1 | IVIC Class 2 | IVIC Class 3 | IVIC Class 4 | IVIC Class 5 | IVIC Class 6 | IVIC Class 7 | IVIC Class S
41 |  | Impulse voltage repetition rate : | Input Data
42 |  | Peak to peak voltage at the fundamental frequency : | Input Data | kV
43 |  | Jump voltage : | Input Data | kV
44 |  | Peak to peak impulse voltage at the impulse voltage repetition rate : | Input Data | kV
45 |  | Impulse voltage rise time : | Input Data | μs
46 |  | Rated thermal short circuit current : | Input Data |  |  |  | Select | 25 | 31.5 | 40 | other
47 |  | Rated peak withstand current : | Input Data | kA peak
48 |  | Stator connection : | Select |  |  |  | Select | star | delta
49 |  | Thermal performance
50 | 8.1 | Thermal class : | F |  |  |  | Select | F | H
51 | 8.1 | Temperature rise class : | B |  |  |  | Select | B | F
52 |  | Starting performance
53 |  | Moment of inertia of the motor (Jm) : | Input Data | kg·m²
54 |  | Operating performance
55 |  | Rated speed : | Input Data | r/min
56 |  | Rated torque : | Input Data | N·m
57 |  | Rated breakdown torque : | Input Data | pu of FLT
58 |  | Voltage at maximum continuous operating speed : | Input Data | V
59 |  | Voltage at minimum continuous operating speed : | Input Data | V
60 |  | Voltage at maximum continuous operating speed at maximum torque : | Input Data | V
61 |  | Current at maximum continuous operating speed : | Input Data | A
62 |  | Current at minimum continuous operating speed : | Input Data | A
63 |  | Current at maximum continuous operating speed at maximum torque : | Input Data | A
64 |  | Efficiency at maximum continuous operating speed : | Input Data | %
65 |  | Efficiency at minimum continuous operating speed : | Input Data | %
66 |  | Efficiency at maximum continuous operating speed at maximum torque. : | Input Data | %
67 |  | Power factor at 100% rated output : | Input Data | pu
68 |  | Power factor at maximum continuous operating speed : | Input Data | pu
69 |  | Power factor at minimum continuous operating speed : | Input Data | pu
70 |  | Power factor at maximum continuous operating speed at maximum torque. : | Input Data | pu
71 |  | Special testing as per S-704 Table 16C
72 | Table 16C | Noise level test at no load : | not required |  |  |  | Select | not required | required | report from identical motor previous test accepted
73 | Table 16C | Measurement of moment of inertia : | not required |  |  |  | Select | not required | required
74 | Table 16C | Measurement of axial shaft displacement : | not required |  |  |  | Select | not required | required
75 | Table 16C | Dielectric dissipation test (tan δ) on stator windings : | not required |  |  |  | Select | not required | required
76 | Table 16C | Partial discharge test on complete stator : | not required |  |  |  | Select | not required | required
77 | Table 16C | Sealed winding conformance test : | not required |  |  |  | Select | not required | required
78 | Table 16C | Unbalanced response test : | not required |  |  |  | Select | not required | required
79 | Table 16C | Bearing housing natural frequency test : | not required |  |  |  | Select | not required | required
80 | Table 16C | Impulse voltage withstand tests of sample coils : | not required |  |  |  | Select | not required | required
81 | 7.5, Table 16C | Dielectric dissipation tests (tan δ) of sample coils : | not required |  |  |  | Select | not required | required
82 | Table 16C | Partial discharge test of sample coils : | not required |  |  |  | Select | not required | required
83 |  | Noise
84 | 9.16.1, 9.16.2, Table 16C | Maximum permissible noise limit : | Input Data | db(A)
85 | 9.16.1, 9.16.2 | Maximum declared motor sound power level at no-load : | Input Data | db(A)
86 | 9.16.1, 9.16.2 | Maximum expected motor sound power level at full load : | Input Data | db(A)
87 |  | Machine construction
88 |  | Motor weight : | Input Data | kg
89 |  | Rotor
90 |  | Rotor weight : | Input Data
91 |  | Terminal box(es)
92 |  | General
93 | 6.8.1 | Ingress protection of all terminal box(es) : | IP55 |  |  |  | Select | IP55 | IP56 | other
94 | 6.8.1 | Confirmation of ingress protection of all terminal box(es) : | Input Data
95 |  | Line conductor terminal box
96 |  | Line conductor terminal box type : | manufacturers standard |  |  |  | Select | manufacturers standard | air insulated | phase insulated with heat shrink insulation | phase insulated with separable connectors | phase separated | phase segregated
97 |  | Line conductor terminal box location : | Select |  |  |  | Select | R | B | L | T
98 |  | Line conductor terminal box cable entries : | Input Data
99 | 11.3.5.4 | Line conductor specification : | Input Data | mm²
100 | 11.7.3, 11.7.4 | Surge protection : | not required |  |  |  | Select | not required | required,
101 | 11.3.5.13 | Portable earth connection point : | Select |  |  |  | Select | Manufacturer's standard | none | 20 mm ball connection | 25 mm ball connection
102 |  | Star point terminal box
103 | 11.3.5.8, 11.8.1 | Star point terminal box required : | Select
104 |  | Space heater terminal box
105 | 11.3.5.15, 11.3.8.3 | Space heater terminal box cable entries : | Select |  |  |  | Select | M20 | M25
106 |  | Space heater supply cable cross-section area : | Select | mm² |  |  | Select | 2.5 | 4 | 6
107 |  | Auxiliary terminal box(es)
108 | 11.3.5.15 | Winding temperature detection terminal box cable entries : | Input Data
109 | 11.3.5.15 | Bearing temperature detection terminal box cable entries : | Input Data
110 | 11.3.5.15 | Vibration detection terminal box cable entries : | Input Data
111 |  | Differential protection
112 | 11.8.1, 11.8.5.9 | Differential protection : | Select |  |  |  | Select | not required | required
113 |  | Bearings (general)
114 | 11.3.7.1.1, 11.3.7.1.2 | Required bearing type : | Select |  |  |  | Select | As per S-704 | sleeve bearings | rolling element bearings
115 | 11.3.7.1.1, 11.3.7.1.2 | D-end bearing type : | Input Data
116 | 11.3.7.1.1, 11.3.7.1.2 | N-end bearing type : | Input Data
117 | 11.3.7.4.1, 11.3.7.4.10 | Lubrication specification : | Input Data
118 | 11.3.7.2.2 | D-end insulated bearing : | Select |  |  |  | Select | not required | required
119 | 11.3.7.1.2 | Driven equipment bearing type : | Select |  |  |  | Select | sleeve bearings | rolling element bearings | unknown
120 | 11.3.7.2.2 | Insulated coupling : | Select |  |  |  | Select | non-insulated coupling | insulated coupling | unknown
121 |  | Sleeve bearings
122 | 9.1.2.2 | Minimum lube oil temperature : | Input Data | °C
123 | 11.3.7.3.9, 9.1.2.2 | Maximum lube oil temperature : | Input Data | °C
124 | 9.1.2.2 | Minimum lube oil pressure : | Input Data
125 | 9.1.2.2 | Maximum lube oil pressure : | Input Data
126 |  | Rolling element bearings
127 |  | Internal clearance : | Select |  |  |  | Select | C3 | C2 | CN | C4 | C5
128 | 11.3.7.4.5, 11.3.7.4.6, 11.3.7.4.7 | Vibration monitoring : | Select |  |  |  | Select | none | SPM nipples
129 | 11.3.7.4.5 | Shock pulse monitoring connection : | Input Data
130 | 11.3.7.4.1 | Relubrication interval : | Input Data | hours
131 |  | Lubrication plate : | Input Data |  |  |  | Select | not required | required
132 |  | Space heaters
133 | 11.3.8.1, 11.3.8.2 | Heater requirement : | required |  |  |  | Select | required | not required
134 | 11.3.8.1 | Supply voltage : | Select | V |  |  | Select | 100-120 | 200-240
135 | 11.3.8.4 | Warning label language : | Select |  |  |  | Select | English | other - see comment
136 |  | Mounting
137 | 11.4.1, Table 23 | Mounting arrangement : | Select |  |  |  | Select | IM B3 (IM 1001) | IM B5 (IM 3001) | IM V1 (IM 3011) | IM V6 (IM 1031) | IM V1 (IM 3015) | IM V6 (IM 1035) | IM B3 (IM 1003) | other
138 |  | Cooling
139 | 11.5.1, Table 24 | Cooling method : | Select |  |  |  | Select | IC4A1A1 | IC5A1A1 | IC6A1A1 | IC8A1W7 | other
140 |  | Air to water heat exchanger
141 | Table 16A, Table 16B | Heat exchanger design code : | Select |  |  |  | Select | EN 13445 | ASME B31.3 | other
142 | 11.5.4.7, 11.5.4.8 | Cooling water specification : | Select |  |  |  | Select | fresh water | salt water
143 | 11.5.4.7, 11.5.4.8 | System material specification : | Input Data
144 | 9.1.2.1 | Maximum cooling water inlet temperature : | Input Data | ° C
145 | 9.1.2.1 | Maximum cooling water inlet pressure : | Input Data | bar
146 | 9.1.2.1 | Minimum cooling water inlet pressure : | Input Data | bar
147 | 9.1.2.1 | Maximum cooling water flow rate : | Input Data | l/s
148 | 9.1.2.1 | Minimum cooling water flow rate : | Input Data | l/s
149 |  | Vibration
150 | 9.1.2.2, 9.1.2.9 | Bearing housing vibration limits : | Select |  |  |  | Select | grade A | grade B | API 541 | other
151 | 11.3.3.3, 11.3.3.4, 9.1.2.2, 9.1.2.6, 9.1.2.7, 9.1.2.8, 9.1.2.9 | Shaft displacement vibration limits : | Select |  |  |  | Select | grade A | grade B | API 541 | other | NA
152 | 11.3.3.3, 11.3.3.4, 9.1.2.2, 9.1.2.6, 9.1.2.7, 9.1.2.8, 9.1.2.9 | Shaft displacement runout limits : | Select |  |  |  | Select | grade A | grade B | API 541 | other | NA
153 | 9.14.1, 9.14.2 | First critical speed : | Input Data | rpm
154 | 11.12 | Lateral vibration analysis : | Select |  |  |  | Select | not required | required
155 | 11.13.1, 11.13.2 | Torsional vibration analysis : | Select |  |  |  | Select | not required | required
156 |  | Surface protection
157 | 11.3.1.6, 11.3.1.7, 11.3.1.8, 11.3.4.1, 11.5.5, 11.6.1, 11.6.2 | Surface protection corrosivity category : | Select |  |  |  | Select | C3 | C4 | C5 | CX
158 | 11.6.3 | Surface protection durability category : | medium (M) 7 to 15 years |  |  |  | Select | medium (M) 7 to 15 years | high (H) 15 to 25 years | very high (VH) +25 years
159 |  | Surface finish : | manufacturer's standard |  |  |  | Select | manufacturer's standard | Norsok M-501 system no.1 | Norsok M-501 system no. 2A | Norsok M-501 system no. 2B
160 |  | Paint colour : | manufacturer's standard |  |  |  | Select | manufacturer's standard | other
161 |  | Temperature monitoring
162 | 11.7.1 | Winding temperature monitoring : | Select |  |  |  | Select | 2 x 3-wire | 3 x 4-wire
163 | 11.3.7.1.3 | Bearing temperature monitoring : | 1 x 3-wire | Pt-100 per bearing |  |  | Select | 1 x 3-wire | 1 x 4 wire | 2 x 3-wire | 2 x 4-wire
164 |  | Winding partial discharge monitoring
165 | 11.3.5.7 | On-line winding partial discharge measurement : | Select |  |  |  | Select | none | capacitive method | inductive method
166 |  | Converter-fed motor data
167 |  | Converter manufacturer : | Input Data
168 |  | Converter model number : | Input Data
169 |  | Motors intended for use in potentially explosive atmospheres
170 | 15.1.1 | Explosion protected motor : | Select |  |  |  | Select | no | yes
171 | 15.1.2 | Hazardous area equipment certifying body : | Select |  |  |  | Select | ATEX | IECEx | EAC | CCC Ex | other
172 | 15.1.3 | Temperature group : | T3 |  |  |  | Select | T3 | T4 | T5 | T6 | T1 | T2
173 | 15.1.3 | Gas group : | IIB |  |  |  | Select | IIB | IIA | IIC
174 | 15.1.2, 15.1.5 | Equipment protection level : | Select |  |  |  | Select | EPL Ga | EPL Gb | EPL Gc | other
175 | 15.1.4, 15.3.1, Table 25 | Classification : | Select |  |  |  | Select | Ex db | Ex db eb | Ex eb | Ex ec | Ex pxb | Ex pyb | Ex pzc
176 | 15.5.1 | tE time at 100% voltage : | Input Data | s
177 |  | tE time at 80% voltage : | Input Data | s
178 |  | Miscellaneous
179 |  | Provision for IoT hardware installation : | Select |  |  |  | Select | required | not required
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C6: Input motor manufacturer.
Note on C7: Input motor model number.
Note on C8: Input motor serial number.
Note on C9: Select order status.
Note on C10: Select CAS level as defined in S-704Q, Annex A. IOGP default is D. CAS level can be raised if more purchaser involvement is required.
Note on C11: Input motor frame size. IEC 60072 series defines preferred frame sizes for a.c. induction motors
Note on C13: Input the duty type as defined in IEC-60034-1 Section 4. IOGP default is S1 for single-speed use. For converter-fed motors, duty S9 or S10 may be applicable, or an S1 duty motor, depending on the load profile.
Note on C14: Select the required number of magnetic poles. For 10 poles and above, select 'other' and enter the required number of poles in the additional comments.
Note on C15: Input the driven load maximum duty power requirement. This value should include any sizing margin requirements.
Note on C16: Select the direction of motor shaft rotation observed when facing the D-end (motor drive end). Default motor direction of rotation is clockwise, when connecting motor terminals U-V-W to supply L1-L2-L3.
Note on C17: Select method of power transfer to driven equipment. Assists with selection of bearings which may be potentially subjected to higher axial or radial loading.
Note on C18: Pulsating torque requirement related to load characteristics such as reciprocating compressor or pump. The manufacturer will ensure the criteria stated in S-704 9.1.3 is met and motor will be subject to torsional analysis report.
Note on C19: Purchaser to input maximum anticipated radial loading on the shaft end for belt driven loads. Supplier to input maximum permissible radial loading if not defined by the Purchaser. Radial forces are those that are perpendicular to the motor shaft.
Note on C20: Purchaser to input maximum anticipated axial loading on the shaft end. Supplier to input maximum permissible axial loading if not defined by the Purchaser. Axial forces are those that are linear to (act along) the motor shaft.
Note on C21: Input the maximum moment of inertia of the load.
Note on C23: Input the motor shaft rated mechanical power output at the defined maximum ambient air temperature.
Note on C24: Confirm the motor full load current whilst operating at rated voltage and rated frequency.
Note on C25: Input the minimum motor operating speed required by driven equipment.
Note on C26: Input the maximum motor operating speed required by driven equipment.
Note on C28: Select location motor shall be situated as per the options available.
Note on C29: Altitude above sea-level. IEC 60034-1 default is 1000 m. Modify 1000 m value only if the site conditions are higher than the IEC default.
Note on C30: IEC 60034-1 default is 40 °C. Modify 40°C value only if the site conditions are higher than the IEC default. 40 °C aligns with the IEC 60079 series default maximum ambient air temperature requirement.
Note on C31: IEC 60034-1 default is -15°C. Modify -15°C value only if the site conditions are lower than the IEC 60034-1 default. -20°C aligns with the IEC 60079 series default minimum ambient air temperature requirement.
Note on C32: Manufacturer to provide details when special packing or controlled storage is required for the transportation and storage conditions detailed by the Purchaser
Note on C33: Purchaser to advise when periods of standstill or storage or transport which exceed 6 months are anticipated, as described in IEC 60034-1 Section 6.6.
Note on C34: IEC 60034-1 Section 6 does not address site humidity. Select the required maximum relative humidity at the maximum ambient air temperature defined in this data sheet.
Note on C35: Select the ingress protection value according to IEC 60034-5. IOGP default is IP55 for 'totally enclosed' motors. NOTE: For interior (indoor) locations, the requirement for a degree of ingress protection lower than IP55 can be evaluated by the user
Note on C36: ​Select the IK code for impact protection with regards to impact energy according to IEC 62262. IOGP default is IK08. This rating will include the motor enclosure and all auxiliary equipment. IEC 60034-1 does not address impact protection.
Note on C38: Purchaser to advise the input voltage, expressed as kV, for which the motor shall be rated.
Note on C39: Select the supply frequency for which the motor shall be rated.
Note on C40: Purchaser to confirm where a motor with insulation class defined in IEC 60034 18-42 Table D.2 is required. Where the purchaser has not made a selection but the motor will be provided with an assigned insulation class this may be confirmed by the supplier
Note on C41: The inverse of the average time between two successive impulses of the same polarity, whether unipolar or bipolar in accordance with IEC 60034 18-42
Note on C42: From converter output data, this is the peak to peak phase to phase voltage at the fundamental frequency in accordance with IEC 60034 18-42
Note on C43: The change in voltage at the terminals of the machine occurring at the start of each impulse in accordance with IEC 60034 18-42. Where double transition is possible, this must be included in the input data.
Note on C44: The peak to peak impulse voltage at the impulse voltage repetition rate in accordance with IEC 60034 18-42
Note on C45: The time for the voltage to rise from 10 % to 90 % of its final value in accordance with IEC 60034 18-42
Note on C46: Confirm the rated short-time thermal withstand current with respect to 0.2 seconds for which the motor shall be rated.
Note on C47: Confirm the rated peak withstand current for which the motor shall be rated.
Note on C48: Confirm configuration of stator winding connection
Note on C50: Select the thermal class of the motor according to IEC 60085. IOGP default is class F.
Note on C51: Select the temperature rise class of motor according to IEC 60085. IOGP default is class B rise (for motors with class F insulation). For class H insulated motors (such as fire-water pump motors) the default is class F rise.
Note on C53: Confirm the motor moment of inertia as defined in IEC 60034-1 Clause 3.24.
Note on C55: Confirm the steady-state asynchronous rotor speed whilst delivering 100% rated power.at the rated voltage and frequency. Note: Includes the slip of the motor at full load and at working temperature.
Note on C56: Confirm the steady-state asynchronous rotor torque whilst delivering 100% rated power.at the rated voltage and frequency.
Note on C57: Confirm the maximum steady-state asynchronous torque which the motor develops without an abrupt drop in speed, when the motor is supplied at the rated voltage and frequency.
Note on C58: Confirm the voltage at motor terminals at maximum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C59: Confirm the voltage at motor terminals at minimum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C60: Confirm the voltage at motor terminals at maximum continuous operating speed at maximum torque as per IEC 61800-4.
Note on C61: Confirm the current at maximum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C62: Confirm the current at minimum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C63: Confirm the current at maximum continuous operating speed at maximum torque as per IEC 61800-4.
Note on C64: Confirm the efficiency at maximum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C65: Confirm the efficiency at minimum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C66: Confirm the efficiency at maximum continuous operating speed at maximum torque as per IEC 61800-4.
Note on C67: Confirm the cosine of the angle between active power and apparent power when the motor is operated at 100% rated power.
Note on C68: Confirm the cosine of the angle between active power and apparent power at maximum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C69: Confirm the cosine of the angle between active power and apparent power at minimum continuous operating speed at upper torque value of the load window as per IEC 61800-4.
Note on C70: Confirm the cosine of the angle between active power and apparent power at maximum continuous operating speed at maximum torque as per IEC 61800-4.
Note on C72: Advise if a noise level test at no load is to be performed. IOGP default is set at 'not required'. Where an identical motor test report from a previous test can be provided, this will be included as an appendix to the test report.
Note on C73: Purchaser to advise if a measurement of moment of inertia test by retardation method is required. JIP33 default is set at 'not required'.
Note on C74: Test to be performed to measure axial shaft displacement.
Note on C75: Dielectric dissipation test (tan δ) for measurement of dielectric losses in stator winding insulation system. Testing to be performed in accordance with IEC 60894 and EN 50209.
Note on C76: Purchaser to advise when a partial discharge measurement on completed winding is required. See API 541 6.3.4.6 for guidance.
Note on C77: Purchaser to advise when a sealed winding conformance test is required. See NEMA MG 1 Part 20 for guidance.
Note on C78: Purchaser to advise when an unbalanced response test is required. See API 541 section 6.3.5.3.
Note on C79: Purchaser to advise when a bearing housing natural frequency test is required. See API 541 section 6.3.5.4.
Note on C80: Purchaser to advise when a sample coil impulse voltage withstand test on 2 sample coils is required.
Note on C81: Purchaser to advise when the dielectric dissipation tests (tan δ) of 2 sample coils is required
Note on C82: Purchaser to advise when partial discharge testing on 2 sample coils is required.
Note on C84: Input the maximum permissible motor A-weighted sound power level at full load including harmonic noise content. Where there is no maximum permissible sound power level state 'NA' in input data.
Note on C85: Confirm the manufacturer declared motor A-weighted sound power level at no-load. IEC 60034-9 Tables 1 and 2 stipulate maximum A-weighted sound power levels at no-load.
Note on C86: Confirm the manufacturer expected A-weighted sound power level, in dB(A) for rated load condition. IEC 60034-9 states that full load noise is not a measured value, but expressed as an expected increase added to the measured no-load value.
Note on C88: Confirm the fully assembled weight of the motor.
Note on C90: Confirm the weight of the rotor, this value is required to facilitate its installation and removal on-site.
Note on C93: Select the ingress protection method according to IEC 60034-5 for which all the terminal box(es) shall be rated.
Note on C94: Supplier to confirm ingress protection method according to IEC 60034-5 for which all the terminal box(es) are rated.
Note on C96: Confirm terminal box specification with regards to design and construction principals. Phase segregated and phase separated designs typically have the capability to eliminate phase to phase faults.
Note on C97: Confirm line conductor terminal box location using coding in accordance with IEC 60034-7
Note on C98: Confirm number, size and type of cable entries in main terminal box e.g. '1 x M32, 2 x M20 cable glands'. State 'un-drilled' where applicable. Where cable entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C99: Confirm line conductor cable size, type and number of cables. E.g. for multi-core cable 3 x 50, for singles 3 x 1 x 50, for multi-cores in parallel 2 x 3 x 50, for singles in parallel 6 x 1 x 50.
Note on C100: Surge protection devices may be installed in the terminal box in the form of surge arresters and surge capacitors to provide protection to the motor insulation from power surges, switching transients, faults and lightning strikes.
Note on C101: Where a fully insulated termination system is not provided confirm where the manufacturer is to provide a connection point on each phase and earth for the attachment of a portable earthing device.
Note on C103: Purchaser to confirm where a separate star point terminal box is required. This is typically used to located differential protection current transformers and to facilitate winding testing activities.
Note on C105: Confirm size of cable entry in main terminal box e.g. 'M20'. State 'un-drilled' where applicable. Where gland entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C106: Where known, purchaser to confirm cross-section area of line conductor to be terminated in the terminal box. Where line conductor cross-section area is not known, the supplier shall confirm maximum connectable cross-section area capacity of terminal box.
Note on C108: Confirm number and size of cable entries in winding temperature detection terminal box e.g. '1 x M25, 1 x M20'. State 'un-drilled' where applicable. Where entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C109: Confirm number and size of cable entries in bearing temperature detection terminal box e.g. '1 x M25, 1 x M20'. State 'un-drilled' where applicable. Where entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C110: Confirm number and size of cable entries in vibration detection terminal box e.g. '1 x M25, 1 x M20'. State 'un-drilled' where applicable. Where entry requirements are not confirmed by purchaser, the supplier will confirm standard offering.
Note on C112: Confirm requirement for pre-installed differential protection current transformers to be provided by the supplier.
Note on C114: Purchaser to confirm required bearing type where it differs from S-704 section 11.3.7.1.2. This may be to correspond with driven equipment bearing type or to accept manufacturer's standard offering where it has been assessed for use.
Note on C115: Confirm the D-end (drive end) bearing model number.
Note on C116: Confirm the N-end (non-drive end) bearing model number.
Note on C117: Confirm the approved lubrication type for the bearing. This will be the grease for rolling element bearings and oil for sleeve bearings.
Note on C118: Select 'required' where d-end bearing insulation is required.
Note on C119: Confirm driven equipment bearing type for consideration when selecting motor bearing type
Note on C120: Purchaser to advise manufacturer where it is known that an insulated coupling is provided, Where an insulated coupling is provided the a shaft grounding system on the N-end of the rotor shaft may be accepted.
Note on C122: Confirm minimum lube oil temperature for which the sleeve bearing is rated to operate.
Note on C123: Confirm maximum lube oil temperature for which the sleeve bearing is rated to operate.
Note on C124: Confirm minimum lube oil pressure for which the sleeve bearing is rated to operate.
Note on C125: Confirm maximum lube oil pressure for which the sleeve bearing is rated to operate.
Note on C127: Confirm the required internal clearance of bearing in accordance with ISO 5753-1 . C3 (group 3) refers to 'greater than normal' clearance as commonly used to avoid too little internal bearing clearance for high voltage motors.
Note on C128: Confirm if there is a requirement for a vibration monitoring connection point to be provided.
Note on C129: Where shock pulse monitoring connection points are to be provided, the purchaser shall confirm site connection type requirement.
Note on C130: Confirm the maximum recommended lubrication interval for where regreasable bearings have been provided. Where regreasing is not applicable input 'N/A' in data field
Note on C131: Confirm when a dedicated lubrication plate is to be attached to the motor stating bearing type, regreasing amount, regreasing intervals and grease product code.
Note on C133: IOGP default position is that space heaters shall be provided.
Note on C134: Input the supply voltage for which the heater shall be rated.
Note on C135: Confirm the language for which the label, warning that heater terminals may be live when the motor is isolated, should be written. Where the language is other than English, this can be confirmed in the 'additional comments' section
Note on C137: Confirm the motor mounting arrangement in accordance with IEC 60034-7.
Note on C139: Confirm the motor cooling method in accordance with IEC 60034-6.
Note on C141: Supplier to confirm design code which the heat exchanger has been manufactured and tested in accordance with.
Note on C142: Confirm specification of cooling water medium
Note on C143: Supplier to confirm system material specification. To be in accordance with S-704 section 11.5.4.
Note on C144: Input maximum cooling water inlet temperature as per project specification and site conditions.
Note on C145: Input maximum cooling water inlet pressure as per project specification and site conditions.
Note on C146: Input minimum cooling water inlet pressure as per project specification and site conditions.
Note on C147: Input maximum cooling inlet water pressure as per project specification and site conditions.
Note on C148: Input minimum cooling water flow rate as per project specification and site conditions.
Note on C150: Input the maximum Bearing housing vibration limits in IEC 60034-14 Table 1 or API 541
Note on C151: Input the maximum shaft displacement vibration limits in IEC 60034-14 Table 1 or API 541.
Note on C152: Input the maximum shaft displacement runout limits in IEC 60034-14 Table 1 or API 541.
Note on C153: Confirm the first speed at which the amplitudes of the vibrations of a machine rotor due to shaft torsional vibration reach their maximum values
Note on C154: Where lateral vibration analysis is required this will be carried out for both FAT (rigid workshop floor) and final site conditions (flexible skid or foundation) in accordance with API 541 clause 4.4.6.2.1.
Note on C155: Torsional vibration analysis will be performed in accordance with API 541 clause 4.4.6.2.2 and IEC 61800-4 clause 9.4.2
Note on C157: Advise surface corrosivity category in accordance with ISO 12944-2 Section 5.1.1.
Note on C158: Advise surface durability category in accordance with ISO 12944-1 Section 5.5. The durability range is not a “guarantee time”. Durability is a technical consideration/planning parameter that can help the owner set up a maintenance programme.
Note on C159: Advise surface finish requirements.
Note on C160: Where standard manufacturer paint colour is unacceptable, confirm specific paint colour requirements in 'additional comments'.
Note on C162: Confirm requirement for embedded temperature monitoring in the stator windings, Use comments section to confirm device transition set-point.
Note on C163: Where required select bearing temperature monitoring devices, these will be provided in pairs to facilitate d-end and n-end temperature monitoring. Use comments section to confirm device transition set-point.
Note on C165: Confirm whether on-line winding partial discharge measurement is required. Typical capacitive method is by coupling capacitors. Typical inductive method include is by rogowski coils. Where further detail is required use the comments field to advise.
Note on C167: Confirm manufacturer of converter from which the machine shall be driven
Note on C168: Confirm model number of converter from which the machine shall be driven.
Note on C170: Confirm whether the motor shall be rated for use in a potentially explosive atmosphere in accordance with IEC 60079
Note on C171: Confirm which certification or notified body shall be accepted for motors to be located in a hazardous area.
Note on C172: Confirm temperature group according to IEC 60079-0 for which machine shall be rated.
Note on C173: Confirm gas group according to IEC 60079-0 for which machine shall be rated.
Note on C174: Confirm equipment protection level (EPL) according to IEC 60079-14
Note on C175: Confirm classification according to IEC 60079 for which motor shall be rated.
Note on C176: time, in seconds, taken for an a.c. rotor or stator winding, when carrying the initial starting current IA, to be heated up to the limiting temperature from the temperature reached at 100% voltage at the maximum ambient temperature
Note on C177: time, in seconds, taken for an a.c. rotor or stator winding, when carrying the initial starting current IA, to be heated up to the limiting temperature from the temperature reached at 80% voltage at the maximum ambient temperature
Note on C179: Where the supplier offers IoT hardware which shall be attached to the motor, mounting points and all other provisions shall be made to facilitate this. Note: This may be to allow the IoT system to be procured at a later date.

## Supplement
Row |  | S-704D Data Sheet for High Voltage Three Phase Cage Induction Motors | Issue
2 | Tag No. : | Insert Tag Number
3 | Service : | Insert Service Description |  | Default
4 | PURCHASE ORDER SPECIFIC REQUIREMENTS
5 | Delete this sheet if not required
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
Public Review Draft

## Guidance
Data Sheet for
High Voltage Three Phase Cage Induction Motors
Guidance on the use of this data sheet
To be used in conjunction with :
IOGP S-704 Supplementary Specification to IEC 60034-1 High Voltage Three Phase Cage Induction Motors.
This data sheet is set-up to be used in electronic format by both the purchaser/user and the supplier/manufacturer.
This data sheet provides reference back to the parent standard or the supplementary specification where relevant.
Default values (if applicable) have been set according to essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement sheet is provided in an open format sheet for application of specific items not covered in the main part of the data sheet. This sheet is not intended to modify requirements defined in the supplementary requirements specification.
The data sheet includes a revision (issue) column on the right hand side for use by the purchaser/user. After the first issue, for each subsequent revision of the data sheet that is issued to suppliers for enquiry or purchase, the purchaser/user should use the issue column to denote that the data on a specific row has been updated since the previous revision. This will enable the supplier to easily identify where changes have been made.
Legend | Select | Supplier/manufacturer completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Supplier/manufacturer completed data entry.
| Select | Purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input data | Purchaser/user completed data entry.
| Select | Either supplier/manufacturer or purchaser/user completed, pick list of pre-defined values (may be pre-populated with a default value).
| Input Data | Either supplier/manufacturer or purchaser/user completed data entry.
| Select | Selection of units from a pre-defined pick list.
Public Review Draft

## Backcover
Month XXXX
Public Review Draft