## Front & Preliminaries
|  |  | SPECIFICATION | July 2026
|  |  | IOGP S-732D | Version 1.1
Procurement Data Sheet for Low Voltage Motor Control Centers (UL)
Revision history
VERSION | DATE | PURPOSE
1.1 | July 2026 | Issued for Public Review
1 | December 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-732D (1.1) Procurement Data Sheet for Low Voltage Motor Control Centers (UL)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-732D (1.1) Procurement Data Sheet for Low Voltage Motor Control Centers (UL)
Introduction
The purpose of this procurement data sheet (PDS) is to specify purchaser-specific requirements for the procurement of low voltage motor control centers in accordance with IOGP S-732 for application in the petroleum and natural gas industries.
The PDS provides requirements where the specification requires the purchaser to define an application-specific requirement. It also includes information required by the purchaser for technical evaluation purposes. Additional purchaser-supplied documents can be listed in the PDS to define scope and technical requirements for enquiry and purchase of the equipment.
The IOGP S-732 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), this PDS, an information requirements specification (IRS) and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Procurement Data Sheet (PDS)
This PDS is to be applied in conjunction with the specification, the IRS and the QRS, referred to in this document as IOGP S-732, IOGP S-732L and IOGP S-732Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Procurement Data Sheet
Row | IOGP S-732D (1.1) Procurement Data Sheet for Low Voltage Motor Control Centers (UL) | [6 empty] | Issue
2 | Ref. clause | Description | Purchaser requirement | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM | Additional notes |  | Requirement CFIHOS ID | Equipment CFIHOS ID
3 |  | General information
4 |  | Conformity assessment system (CAS) level : | D |  | D | [5 empty] | select | A | B | C | D
5 |  | Site conditions
6 | 7.2 | Ambient air temperature - upper limit : | 40 | °C | 40 | °C |  |  |  |  | select | 40 | 45 | 50
7 | 7.2 | Ambient air temperature - lower limit : | 0 | °C | 0 | °C |  |  |  |  | select | 0 | -20 | -30 | -40
8 | 7.2 | Altitude of installation : | ≤ 1 000 (3 300) | m (ft) | ≤ 1 000 (3 300) | m (ft) |  |  |  |  | select | ≤ 1 000 (3 300) | ≤ 2 000 (6 600) | other
9 | 7.2 | Humidity limit : | < 95 | % | < 95 | % |  |  |  |  | select | < 95 | other
10 | 8.1.2.7 | Seismic design : | not required |  | not required | [5 empty] | select | not required | required
11 | 8.1.2.7 | Site location : | input data |  | input data
12 | 8.1.2.7 | Risk category : | not applicable |  | not applicable | [5 empty] | select | not applicable | I | II | III | IV
13 | 8.1.2.7 | Component importance factor (Ip) : | not applicable |  | not applicable | [5 empty] | select | not applicable | 1 | 1.25 | 1.5
14 | 8.1.2.7 | Site class : | not applicable |  | not applicable | [5 empty] | select | not applicable | A | B | C | D | E | F
15 | 8.1.2.7 | Seismic certificate : | not required |  | not required | [5 empty] | select | not required | required
16 |  | Location installation : | indoor - climate controlled |  | indoor - climate controlled | [5 empty] | select | indoor - climate controlled | indoor - ventilated | outdoor
17 | 7.3 | Application/operating environment : | onshore |  | onshore | [5 empty] | select | onshore | offshore - fixed | offshore - floating | marine (ship) | other
18 | 8.2.6, 8.2.6.2, 8.2.6.3 | Environmental contamination : | not required |  | not required | [5 empty] | select | not required | salt-laden | H2S | salt-laden and H2S | other
19 | 1.1.1, 5.1.5, 7.3 | Certification (additional) : | not required |  | not required | [5 empty] | select | not required | USCG/ABS | other
20 | 8.1.2.8.1, 8.1.2.8.3 | Arc resistant certification : | third-party certified |  | third-party certified | [5 empty] | select | third-party certified | self-declared | not applicable
21 |  | Electrical power parameters
22 | 5.1.1, 5.1.2 | Voltage : | 480 | V | 480 | V |  |  |  |  | select | 208 | 480 | 600 | other
23 | 5.1.1, 5.1.2 | Frequency : | 60 | Hz | 60 | Hz |  |  |  |  | select | 50 | 60 | other
24 | 5.1.1, 5.1.2 | Phase/wire : | 3-phase 3-wire |  | 3-phase 3-wire | [5 empty] | select | 3-phase 3-wire | 3-phase 4-wire | 1-phase 2-wire | other
25 | 6.3.17, 6.3.18 | System grounding : | high resistance |  | high resistance | [5 empty] | select | high resistance | solid | ungrounded
26 | 5.4.4.3 | Available fault current (symmetrical) : | input data | kA | input data | kA
27 | 5.4.4.3 | System X/R ratio : | input data |  | input data
28 | Table 1 | System connection : | wye |  | wye | [5 empty] | select | wye | delta | other
29 |  | MCC structure
30 | 6.2.3 | Arc resistant construction : | Type 2 |  | Type 2 | [5 empty] | select | Type 2 | not required
31 | 8.1.2.8.5 | Arc plenum : | not required |  | not required | [5 empty] | select | not required | plenum interior exhaust | plenum exterior exhaust
32 | 6.2.1, 8.1.2.1, 8.1.2.3, 8.1.2.4 | NEMA enclosure rating : | Type 1 with gasket |  | Type 1 with gasket | [5 empty] | select | Type 1 with gasket | Type 12 | Type 3R (non walk-in) | other
33 | H.7.1 | Section depth : | 50 cm (20 in) |  | 50 cm (20 in) | [5 empty] | select | 50 cm (20 in) | 40 cm (15 in) | other
34 | 8.2.29.3.8.1, 8.2.29.3.8.2 | Vertical wireway width : | standard |  | standard | [5 empty] | select | standard | wide
35 | 8.2.6 | Enclosure paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | ANSI 61
36 | 8.2.6 | Unit paint color : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | white
37 | 8.2.9.10 | Back-to-back arrangement : | not required |  | not required | [5 empty] | select | not required | required
38 | 8.2.40.1.2, 8.2.40.1, 8.2.40.1.1, 8.2.40.1.3, 8.2.40.1.4 | Space heater : | not required |  | not required | [5 empty] | select | not required | required
39 | 8.2.40.1.3, 8.2.40.1.4, 8.2.40.2, 8.2.40.2.1, 8.2.40.2.2, 8.2.40.2.3, 8.2.40.2.4, 8.2.40.2.5 | Space heater control : | not applicable |  | not applicable | [5 empty] | select | not applicable | fixed (constant ON) | thermostat | hygrostat
40 | 8.1.2.3, 8.1.2.4 | Outgoing cables : | top |  | top | [5 empty] | select | top | bottom
41 |  | Incoming line section
42 | 8.2.35.2, 8.2.35.3 | Cable/bus entry location : | top |  | top | [5 empty] | select | top | bottom | transition section
43 | 8.2.19.1, 8.2.20.1 | Service entrance application : | no |  | no | [5 empty] | select | no | yes
44 | 5.3.1.1, 8.2.35.2, 8.2.35.3 | Incoming line termination : | select |  | select | [5 empty] | select | circuit breaker | main lugs only | fusible disconnect | bus connection
45 | 8.2.35.5 | Incoming line metering : | not required |  | not required | [5 empty] | select | not required | required
46 | 1.3.1 | Circuit breaker : | not required |  | not required | [5 empty] | select | not required | required
47 | 1.3.1 | Circuit breaker type : | not applicable |  | not applicable | [5 empty] | select | not applicable | molded case circuit breaker (MCCB) | insulated case circuit breaker (ICCB) | printed circuit board (PCB) breaker
48 | 1.3.1 | Protection type : | not applicable |  | not applicable | [5 empty] | select | not applicable | thermal magnetic | trip unit-LSI | trip unit-LSIG | trip unit-LI
49 | 1.3.2 | Separate main breaker control compartment : | required |  | required | [5 empty] | select | not applicable | required | not required
50 | 1.3.2 | Arc reducing maintenance switch : | not applicable |  | not applicable | [5 empty] | select | not applicable | required | not required
51 | 8.2.16.2 | Cable entry : | select |  | select | [5 empty] | select | required | not required
52 | 8.2.35.2, 8.2.35.3 | Conductor size : | input data | AWG | input data | AWG
53 | 8.2.35.2, 8.2.35.3 | Conductor material : | select |  | select | [5 empty] | select | copper | aluminum
54 | 8.2.35.2, 8.2.35.3 | Number of conductors per phase : | select | no. | select | no. |  |  |  |  | select | 1 | 2 | 3 | 4 | other
55 | 8.2.31.2, 8.2.34.1.1 | Incoming cable grounding conductor size : | input data | AWG | input data | AWG
56 | 8.2.34.1.1 | Number of incoming cable grounding conductors : | input data | no. | input data | no.
57 | 8.2.35.4 | Bus duct entry : | select |  | select | [5 empty] | select | required | not required
58 | 8.2.35.4 | Cable bus entry : | select |  | select | [5 empty] | select | required | not required
59 |  | Bus
60 | 5.1.1, 5.1.2, 5.3.2 | Horizontal bus rating : | select | A | select | A |  |  |  |  | select | 600 | 800 | 1 000 | 1 200 | 1 600 | 2 000 | 2 500 | 3 000 | 3 200
61 | 5.1.1, 5.1.2, 5.4.1.1, 5.4.1.2 | Rated short-circuit current : | 42 | kA | 42 | kA |  |  |  |  | select | 42 | 65 | 100 | other
62 | 5.4.1.4, 5.4.4.2 | Rated short-time current rating duration : | 0.05 | s | 0.05 | s |  |  |  |  | select | 0.05 | other | not applicable
63 | 5.3.2.1, 8.2.9.1 | Power bus plating material : | tin |  | tin | [5 empty] | select | tin | silver | none
64 | 8.2.9.12, 8.2.9.7 | Insulated main horizontal bus : | not required |  | not required | [5 empty] | select | not required | required
65 | 5.1.1, 5.3.3 | Vertical bus rating : | 600 | A | 600 | A |  |  |  |  | select | 300 | 600 | 800 | 1 200
66 | 8.2.22.1, 5.1.1, 8.2.9.3 | Neutral bus rating : | not required |  | not required | [5 empty] | select | not required | full | half
67 | 8.2.20.11 | Neutral bus load termination point (location) : | not applicable |  | not applicable | [5 empty] | select | not applicable | all sections | incoming section only
68 | 8.2.34.1.1, 8.2.34.1.3, 8.2.34.1.4, 8.2.34.1.5 | Horizontal ground bus (location) : | bottom |  | bottom | [5 empty] | select | bottom | top
69 | 8.2.34.1.1, 8.2.34.1.2 | Horizontal ground bus rating : | 300 | A | 300 | A |  |  |  |  | select | 300 | 600 | Table 24
70 |  | Combination motor controller unit
71 | 8.2.11.16.1, 8.2.11.16.2, 8.2.11.16.3, 8.2.11.17.1, 8.2.11.17.2, 8.2.11.17.3, 8.2.11.17.4, 8.2.11.17.5, 8.2.11.17.6, 8.2.11.18 | Overload relay type : | microprocessor |  | microprocessor | [5 empty] | select | microprocessor | solid-state | mechanical | multiple types
72 | 8.2.11.17.6, 8.2.12.3 | Unit disconnect type : | motor circuit protector (MCP) |  | motor circuit protector (MCP) | [5 empty] | select | motor circuit protector (MCP) | molded case circuit breaker (MCCB) | fused disconnect
73 | 8.2.11.25.1, 8.2.11.25.2, 8.2.11.25.3, 8.2.11.25.4 | Control power source : | individual unit control power transformer (CPT) |  | individual unit control power transformer (CPT) | [5 empty] | select | individual unit control power transformer (CPT) | 24 Vdc power supply | external
74 | 5.2.1 | Control circuit voltage : | 120 Vac |  | 120 Vac | [5 empty] | select | 120 Vac | 24 Vdc
75 | 8.2.11.21, 8.2.11.22, 8.2.11.23 | Control power transformer (CPT) capacity : | standard capacity |  | standard capacity | [5 empty] | select | extra capacity | standard capacity
76 | 8.2.11.28 | Minimum motor size for space heater : | not required | hp | not required | hp |  |  |  |  | select | not required | ≥5 | ≥10 | ≥20 | ≥50 | ≥100 | other
77 | 8.2.11.8, 8.2.37.5, 8.2.42.1.1, 8.2.42.1.2, 8.2.42.1.3 | Status indicator lights : | run-stopped |  | run-stopped | [5 empty] | select | not required | run-stopped | run-stopped-trip
78 | 8.2.42.2 | Unit stop pushbutton : | not required |  | not required | [5 empty] | select | not required | momentary | maintained
79 | 8.2.11.30 | Auto trip reset : | not required |  | not required | [5 empty] | select | not required | required
80 | 8.2.11.18 | Trip reset : | select |  | select | [5 empty] | select | local | remote | both local and remote
81 |  | Interface with control systems
82 | 8.2.11.18, 8.2.35.5 | Intelligent electronic device (IED) brand : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | other
83 | 8.2.41.1 | Process control interface (ICSS/DCS) media : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | not required | hardwired discrete | serial cable | Ethernet (Cu) | Ethernet (fiber) | multiple | other | to be provided later
84 | 8.2.41.1 | Process control interface (ICSS/DCS) protocol : | select |  | select | [5 empty] | select | not required | volt-free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 (all parts) | Modbus TCP/IP | Profinet | Profibus | multiple | other | to be provided later
85 | 8.2.41.1 | Process control interface (ICSS/DCS) network redundancy : | select |  | select | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other | to be provided later
86 | 8.2.41.1 | Electrical control interface (ECMS) media : | not required |  | not required | [5 empty] | select | manufacturer's standard | not required | hardwired discrete | serial cable | Ethernet (Cu) | Ethernet (fiber) | other | to be provided later
87 | 8.2.41.1 | Electrical control interface (ECMS) protocol : | not required |  | not required | [5 empty] | select | not required | volt-free contact / 4-20mA | DeviceNet | EtherNet/IP | IEC 61850 | Modbus TCP/IP | Profinet | Profibus | other | to be provided later
88 | 8.2.41.1 | Electrical control interface (ECMS) network redundancy : | not applicable |  | not applicable | [5 empty] | select | not applicable | no redundancy | parallel redundancy protocol (PRP) | high-availability seamless redundancy (HSR) | other | to be provided later
89 | 8.2.11.18, 8.2.35.5 | Intelligent electronic device (IED) remote configuration via ECMS : | not applicable |  | not applicable | [5 empty] | select | not applicable | not required (local at IED only) | required | other | to be provided later
90 | 8.2.42.2, 8.2.42.3 | Communication system power supply : | not required |  | not required | [5 empty] | select | not required | internal simplex | internal redundant | external simplex | external redundant
91 |  | Accessories
92 | 8.2.11.18, 8.2.35.5 | Application software : | required |  | required | [5 empty] | select | required | not required
93 | 8.2.43.1, 8.2.43.2, 8.2.43.3 | Continuous thermal monitoring : | not required |  | not required | [5 empty] | select | not required | required
94 | 8.2.43.1, 8.2.43.2, 8.2.43.3 | Thermal monitoring analytical software : | not required |  | not required | [5 empty] | select | not required | required
95 | 8.2.4.8 | Thermal scanning inspection windows : | not required |  | not required | [5 empty] | select | not required | required
96 | 8.2.10.5 | Absence of voltage tester : | not required |  | not required | [5 empty] | select | not required | incoming line section | each unit | incoming line section and each unit
97 | 8.3.4 | Undervoltage ridethrough : | not required |  | not required | [5 empty] | select | not required | required
98 | 8.1.2.8.8 | Arc resistant blank unit (quantity per unit size) : | 1 |  | 1 | [5 empty] | select | not required | 1 | 2 | 3 | other
99 | 8.2.21.1 | Ground fault detection : | not required |  | not required | [5 empty] | select | not required | phase detection indicators | indicating meter | pulsing system | unit detection
100 | 8.2.2.10 | Ventilation filters : | not required |  | not required | [5 empty] | select | not required | required
101 |  | Shipping and preservation
102 | H.5.2, H.5.3, H.5.4 | Equipment preservation : | manufacturer's standard |  | manufacturer's standard | [5 empty] | select | manufacturer's standard | special
103 | H.5.2, H.5.3, H.5.4 | Provisions for energizing space heaters for storage : | not required |  | not required | [5 empty] | select | not required | required
104 | H.5.1 | Desiccant bags installed for shipping : | not required |  | not required | [5 empty] | select | not required | incoming only | each unit
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Note on C4: Select the conformity assessment level of this equipment. The default selection of CAS level D is typically used for trusted manufacturers with which the purchaser has experience. For CAS level selection guidance, refer to IOGP S-732Q. Default value : D
Note on C6: Select the upper limit ambient air temperature measured outside of the enclosure. The default value as per UL 845 is 40 °C with the 24 h average not exceeding 35 °C. Default value : 40
Note on C7: Select the lower limit ambient air temperature. The default value as per UL 845 is 0 °C. Default value : 0
Note on C8: Select the LV MCC installation altitude. UL 845 is based on the altitude not to exceed 2 000 m (6 600 ft) or 1 000 m (3 300 ft) if the equipment includes solid-state controllers. If "other" selected, specify the details in the "Additional notes" column. Default value : ≤ 1 000 (3 300)
Note on C9: Select the humidity limit. As per UL 845, default value measured over 24 h not to exceed 95 % non-condensing. If "other" is selected, specify the humidity in the "Additional notes" column. Default value : < 95
Note on C10: Select the seismic design requirement as per ASCE/SEI 7-16. Default value : not required
Note on C11: Specify the site physical address or latitude and longitude to determine the seismic acceleration values.
Note on C12: Specify the risk category as per ASCE/SEI 7-16 (risk category of buildings and other structures for flood, wind, snow, earthquake and ice loads). The typical oil and gas category is IV. Default value : not applicable
Note on C13: Specify the component importance factor of buildings and other structures for snow, ice, and earthquake loads. The typical oil and gas importance factor is 1.5. Default value : not applicable
Note on C14: Specify the site class as per ASCE/SEI 7-16. Site class D to be specified if the detailed soil properties are not known. Default value : not applicable
Note on C15: Select whether the seismic certificate provided by a third party is required. Default value : not required
Note on C16: Select the installation location of the LV MCC. Default value : indoor - climate controlled
Note on C17: Select the operating environment for the LV MCC. If "other" is selected, specify the operating environment in the "Additional notes" column. Default value : onshore
Note on C18: Select any contaminant exposure to the LV MCC. If "other" is selected, specify the contaminant exposure in the "Additional notes" column. Default value : not required
Note on C19: Select certification requirements (in addition to NRTL or ACO). If "other" is selected, specify the additional certification in the "Additional notes" column. Default value : not required
Note on C20: Select the required certification for arc resistance testing. Default value : third-party certified
Note on C22: Refer to Table 1. If "other" is selected, specify the voltage in the "Additional notes" column. Default value : 480
Note on C23: If "other" is selected, specify the frequency in the "Additional notes" column. Default value : 60
Note on C24: If "other" is selected, specify the phase in the "Additional notes" column. Default value : 3-phase 3-wire
Note on C25: Select the grounding system of the facility to which the LV MCC will be connected to. Default value : high resistance
Note on C26: Specify the available fault current (symmetrical) of the system at the LV MCC.
Note on C27: Specify the X/R ratio (system reactance / system resistance). Higher X/R ratios can result in de-rating of short circuit ratings.
Note on C28: Select the system connection. If "other" is selected, specify the system connection in the "Additional notes" column. Default value : wye
Note on C30: Select whether the LV MCC requires arc resistant construction that is verified through testing for internal arcing faults. Arc resistant Type 2 enclosures provide protection for personnel and improve electrical safety. Default value : Type 2
Note on C31: Select whether an arc plenum for exhaust is required due to the arrangement or configuration of the room or space where the LV MCC is located. A plenum design may not be available from all manufacturers. Default value : not required
Note on C32: Select the NEMA enclosure rating. If "other" is selected, specify the system connection in the "Additional notes" column. Default value : Type 1 with gasket
Note on C33: Select the section nominal depth. The 50 cm (20 in) depth is preferred to ensure adequate wiring space. If "other" is selected, specify the required nominal section depth in the "Additional notes" column. Default value : 50 cm (20 in)
Note on C34: Vertical wireway widths vary among manufacturers. Typically, the standard nominal width is 100 mm (4 in). Consult with manufacturer for the additional widths provided with the "wide" option. Default value : standard
Note on C35: Select the enclosure paint color. Default value : manufacturer's standard
Note on C36: Select the paint color for the unit interior. Units are normally the same color as the enclosure. "White" can be selected to enhance visibility. Default value : manufacturer's standard
Note on C37: Select whether two separate LV MCC assemblies connected through a transition section are required (back-to-back LV MCC arrangement). Default value : not required
Note on C38: Select whether section space heaters are required. Default value : not required
Note on C39: If space heaters are required, select controls type. Default value : not applicable
Note on C40: Select the location of outgoing cables. Default value : top
Note on C42: Select the incoming cable entry location. Default value : top
Note on C43: Select whether the LV MCC is designated as service entrance equipment. Refer to Annex G for the service entrance requirements. Default value : no
Note on C44: Select the incoming line termination type. Although "main lugs only" can be the most cost effective option, arc resistant designs can require a current limiting breaker or fuse.
Note on C45: Default value : not required
Note on C46: Select whether a main circuit breaker is required. If required, complete rows 47, 48 and 49. Default value : not required
Note on C47: If a circuit breaker is specified, select the type of circuit breaker required. Molded case circuit breaker (MCCB) is the type that is typically supplied. Default value : not applicable
Note on C48: If a circuit breaker is specified, select the protection type. Thermal magnetic is the typical protection type for MCCB. LI (long time and instantaneous) is the typical protection type for ICCB and PCB. Default value : not applicable
Note on C49: Select whether a separate main breaker control compartment is required (e.g. for power supplies and/or fuses). Default value : required
Note on C50: Available only with a circuit breaker that is equipped with an integral trip unit. Default value : not applicable
Note on C51: Select whether cable entry is required. If required, complete rows 52 through 56.
Note on C52: If the cable entry is required, specify the conductor size needed for the incoming service.
Note on C53: If the cable entry is required, specify the conductor material. Copper is typically used.
Note on C54: If the cable entry is required, specify the number of conductors per phase. If "other" is selected, specify the number of conductors in the "Additional notes" column.
Note on C55: If the cable entry is required, specify the size of the incoming cable grounding conductor.
Note on C56: If the cable entry is required, specify the number of the incoming cable grounding conductors.
Note on C57: Select whether the bus duct entry is required. If required, LV MCC manufacturer to provide the details of the bus duct (ampacity, size, dimensions, number of bus bars, etc.).
Note on C58: Select whether the cable bus entry is required. If required, LV MCC manufacturer to provide the details of the cable duct (ampacity, size, dimensions, number of cables, etc.).
Note on C60: Select the main bus rating. For 2 500 A and above, arc resistance may not be available.
Note on C61: Select the power bus short-circuit current rating. For "other" ratings, refer to Table 3 and specify the value in the "Additional notes" column. The standard duration for the SC test is three cycles. Default value : 42
Note on C62: Select the short-time testing duration if optional short-time testing is specified. If "other" is selected, specify the time based on Table 45. Default value : 0.05
Note on C63: Select the bus plating material. If "none" is selected, the ampacity and temperature rise will be affected. Tin is preferred over silver in corrosive gas applications. Default value : tin
Note on C64: Select the main bus insulation requirement. Insulated main horizontal bus with insulated shipping split connections provides a higher degree of electrical safety and ingress protection. Default value : not required
Note on C65: Select the vertical bus rating. This will be the value for all vertical buses in the LV MCC assembly. Default value : 600
Note on C66: Select the neutral bus rating. When a neutral bus is required a full size neutral is recommended. Default value : not required
Note on C67: Select the location(s) where the neutral from outgoing load feeder cables will be connected in the LV MCC assembly. The selection of "incoming section" will require the load neutral feeder wire to be routed to the incoming section for connection. Default value : not applicable
Note on C68: Select the ground bus location. The entry location of the incoming field wiring should be considered when selecting the location of the ground bus. Default value : bottom
Note on C69: Select the horizontal ground bus rating for values different than 300 A and 600 A. Refer to Table 24 and Table 25. Default value : 300
Note on C71: Select the overload relay type. For multiple types, specify additional information on the "Supplement" tab or project drawings. Default value : microprocessor
Note on C72: Select the unit disconnect type. If "fused disconnect" is selected, this type disconnect is normally provided for all units (motor controllers, feeders, contactors, etc.). Default value : motor circuit protector (MCP)
Note on C73: Select the control power source. The voltage level for control power should not exceed 120 V nominal. Default value : individual unit control power transformer (CPT)
Note on C74: Select the control power voltage. Default value : 120 Vac
Note on C75: Select the CPT capacity. If "extra capacity" is selected, 50 VA additional capacity is included in the sizing as per the supplementary specification. Default value : standard capacity
Note on C76: Select the minimum size motor for which provisions for motor space heater control is required. These motor sizes are provided to promote standardization. Other requirements can be specified in the "Additional notes" column. Default value : not required
Note on C77: Select the indicator lights requirements. Additional status indicator lights can be specified on the project drawings or in the "Additional notes" column, but it will reduce standardization. Default value : run-stopped
Note on C78: Select the requirement to add a stop pushbutton installed on the door (device panel) of each combination motor controller unit. Default value : not required
Note on C79: Select the requirement for the auto-trip-reset capability. Default value : not required
Note on C80: Select the requirement for the trip-reset capability.
Note on C82: Select "other" if the operating company or the site has a default IED brand for operational and/or system integration commonality at that location. If "other" is selected, specify the IED manufacturer/range in the "Additional notes" column. Default value : manufacturer's standard
Note on C83: Select the communication media within the assembly for interface to the process control system. If "multiple" or "other" is selected, specify details in the "Additional notes" column and on the project drawings. Default value : manufacturer's standard
Note on C84: Select the communication protocol within the assembly for the stated media interface to the process control system. If "multiple" or "other" is selected, specify details in the "Additional notes" column and on the project drawings.
Note on C85: PRP or HSR (refer to IEC 62439-3) provides seamless failover against failure of a network component for most industrial Ethernet protocols. If "other" is selected, specify the redundancy protocol in the "Additional notes" column.
Note on C86: If required, select the communication media within the assembly for interface to the electrical control and management system. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C87: If required, select the communication protocol within the assembly for the stated media interface to the electrical control and management system. If "other" is selected, specify details in the "Additional notes" column. Default value : not required
Note on C88: PRP or HSR (refer to IEC 62439-3) provides seamless failover against failure of a network component for most industrial Ethernet protocols. If "other" is selected, specify the redundancy protocol in the "Additional notes" column. Default value : not applicable
Note on C89: Not applicable if an ECMS is not specified. Where required, this is an optional facility provided by the electrical control system / power management system to remotely edit IED protection and logic settings by a user with the correct system privileges. Default value : not applicable
Note on C90: Select the level of desired redundancy, including auxiliary power to the data switches and other miscellaneous communication equipment. To be supplied by others if "external" is selected. Refer to project drawings for additional details. Default value : not required
Note on C92: Select whether the application software for configuration of digital programmable devices is required. Specify other requirements in the "Additional notes" column. This includes any nonstandard interface cables but not any computer hardware. Default value : required
Note on C93: Default value : not required
Note on C94: Select whether thermal monitoring analytical software is required. This includes any nonstandard interface cables but does not include any computer hardware. Default value : not required
Note on C95: Select whether thermal scanning inspection windows are required. Manufacturer to specify the recommended location. Default value : not required
Note on C96: Select the requirement and location for absence of voltage tester devices. The installation of these devices in each unit can be used to establish an electrically safe work condition and assist with LOTO procedures. Refer to NFPA 70E. Default value : not required
Note on C97: Select whether undervoltage ridethrough is required. Manufacturer to specify the voltage and time parameters for each starter size. Default value : not required
Note on C98: Select the number of blanks per unit size. If "other" is selected, use the "Additional notes" column for details. The blank unit is used to maintain the arc resistant rating of the LV MCC when a unit is removed for maintenance. Default value : 1
Note on C99: The selections for "phase indicators", "meter" and "pulsing" are for the incoming section only. The selection for "unit detection" allows for identifying which unit has a ground fault. Default value : not required
Note on C100: Select whether ventilation filters are required. Default value : not required
Note on C102: Select the equipment preservation requirement. The manufacturer's standard shipping is appropriate for domestic shipping (not offshore) and indoor storage. If "special" is selected, specify details in the "Additional notes" column or "Supplement" tab. Default value : manufacturer's standard
Note on C103: Select whether provisions for energizing space heaters for storage are required. If required, the preservation packaging will allow for access to the space heater connections without compromising the preservation integrity. Default value : not required
Note on C104: Select whether desiccant bags for shipping are required. Default value : not required

## Supplement
Row | IOGP S-732D (1.1) Procurement Data Sheet for Low Voltage Motor Control Centers (UL) | Issue
2 | Purchase order specific requirements
3 | Delete this sheet if not required.
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
Public Review Draft

## Guidance
IOGP S-732D (1.1) Procurement Data Sheet for Low Voltage Motor Control Centers (UL)
Guidance on the use of this procurement data sheet (PDS)
This PDS is to be used in conjunction with IOGP S-732, Supplementary Specification to UL 845 for Low Voltage Motor Control Centers.
This PDS is designed to be used in MS Excel electronic format by the purchaser and the supplier.
This PDS, completed with requested values, should be delivered back to the purchaser by using the PDS template or other mutually agreed method.
The Ref. clause column provides references back to the following: — parent standard and/or supplementary specification when the PDS is used in conjunction with a supplementary specification; — specification when the PDS is used in conjunction with a standalone specification.
Guidance specific to an item may be provided as a note in the description. This guidance is meant to provide a better understanding of the PDS item and/or an explanation of how to complete the input.
The Additional notes column may be used by the purchaser or supplier to provide additional information pertinent to the specification and/or supply of the equipment.
The Issue column should be used by the purchaser for revision purposes. After the first issue, for each subsequent revision of the PDS that is issued to suppliers for enquiry or purchase, the purchaser should use this column to denote that the data in a specific row has been updated since the previous revision. This enables the supplier to easily identify where changes have been made.
Default values (if applicable) have been set in accordance with essential minimum requirements as an integral part of this specification and should only be changed where specific justification can be provided.
The Supplement worksheet is provided in an open format for application of specific items not covered in the main part of the PDS. This worksheet is not intended to modify requirements defined in the specification.
The Purchaser requirement and Purchaser requirement UOM columns specify the functional and early design requirements of the equipment. Specified requirements allow the supplier to provide an offer to the purchaser.
The Supplier offered value and Supplier offered UOM columns are used by the supplier to declare the offered value. Where the offered product characteristic differs from the purchaser requirement, the cell shading is automatically updated (by conditional formatting) to highlight the deviation from the purchaser requirement.
The Requirement CFIHOS ID and Equipment CFIHOS ID in columns K and L enable information exchange in a data-centric manner. Note that these columns are in a hidden area of the worksheet and can be unhidden for use.
Legend
select | Purchaser completed, drop-down list of pre-defined values (may be prepopulated with a default value)
input data | Purchaser completed data entry
select | Supplier completed, drop-down list of pre-defined values
input data | Supplier completed data entry
select | Either supplier or purchaser completed, drop-down list of predefined values (may be prepopulated with a default value)
input data | Either supplier or purchaser completed data entry
select | Selection of units from a pre-defined drop-down list
select | No input expected
input data | No input expected
UOM | Fixed unit of measure
UOM | Fixed unit of measure
No unit of measure (null)
Configuration of purchaser and supplier input columns
The following table, to be read alongside the above legend, shows the possible combinations of relationships between purchaser requirement and supplier offered values.
Purchaser requirement |  | Purchaser requirement UOM | Supplier offered value | Supplier offered UOM
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
select |  | select | select | select
input data |  | select | input data | select
select |  | UOM | select | UOM
input data |  | UOM | input data | UOM
select |  |  | select
input data |  |  | input data
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft