## Front & Preliminaries
|  |  | SPECIFICATION | July 2026
|  |  | IOGP S-732L | Version 1.1
Information Requirements for Low Voltage Motor Control Centers (UL)
Revision history
VERSION | DATE | PURPOSE
1.1 | July 2026 | Issued for Public Review
1 | December 2020 | First Edition
Acknowledgements
This IOGP Specification was prepared by a Joint Industry Programme 33
Standardization of Equipment Specifications for Procurement organized
by IOGP with support by the World Economic Forum (WEF).
Disclaimer
Whilst every effort has been made to ensure the accuracy of the information
contained in this publication, neither IOGP nor any of its Members past present or
future warrants its accuracy or will, regardless of its or their negligence, assume
liability for any foreseeable or unforeseeable use made thereof, which liability is
hereby excluded. Consequently, such use is at the recipient’s own risk on the basis
that any use by the recipient constitutes agreement to the terms of this disclaimer.
The recipient is obliged to inform any subsequent recipient of such terms.
Please note that this publication is provided for informational purposes and
adoption of any of its recommendations is at the discretion of the user. Except as
explicitly stated otherwise, this publication must not be considered as a substitute
for government policies or decisions or reference to the relevant legislation relating
to information contained in it.
Where the publication contains a statement that it is to be used as an industry
standard, IOGP and its Members past, present, and future expressly disclaim all
liability in respect of all claims, losses or damages arising from the use or
application of the information contained in this publication in any industrial application.
Any reference to third party names is for appropriate acknowledgement of their
ownership and does not constitute a sponsorship or endorsement.
Copyright notice
The contents of these pages are © International Association of Oil & Gas Producers.
Permission is given to reproduce this report in whole or in part provided (i)
that the copyright of IOGP and (ii) the sources are acknowledged. All other rights are
reserved. Any other use requires the prior written permission of IOGP.
These Terms and Conditions shall be governed by and construed in accordance
with the laws of England and Wales. Disputes arising here from shall be exclusively
subject to the jurisdiction of the courts of England and Wales.
IOGP S-732L (1.1) Information Requirements for Low Voltage Motor Control Centers (UL)
Foreword
This specification was prepared under Joint Industry Programme 33 (JIP33) "Standardization of Equipment Specifications for Procurement" organized by the International Oil & Gas Producers Association (IOGP) with the support from the World Economic Forum (WEF). Companies from the IOGP membership participated in developing this specification to leverage and improve industry level standardization globally in the oil and gas sector. The work has developed a minimized set of supplementary requirements for procurement, with life cycle cost in mind, resulting in a common and jointly agreed specification, building on recognized industry and international standards.
Recent trends in oil and gas projects have demonstrated substantial budget and schedule overruns. The Oil and Gas Community within the World Economic Forum (WEF) has implemented a Capital Project Complexity (CPC) initiative which seeks to drive a structural reduction in upstream project costs with a focus on industry-wide, non-competitive collaboration and standardization. The CPC vision is to standardize specifications for global procurement for equipment and packages. JIP33 provides the oil and gas sector with the opportunity to move from internally to externally focused standardization initiatives and provide step change benefits in the sector's capital projects performance.
This specification has been developed in consultation with a broad user and supplier base to realize benefits from standardization and achieve significant project and schedule cost reductions.
The JIP33 work groups performed their activities in accordance with IOGP's Competition Law Guidelines (November 2020).
IOGP S-732L (1.1) Information Requirements for Low Voltage Motor Control Centers (UL)
Introduction
The purpose of this information requirements specification (IRS) is to specify information requirements for the procurement of low voltage motor control centers in accordance with IOGP S-732 for application in the petroleum and natural gas industries.
The IRS defines the information requirements, including format, timing and purpose, to be provided by the supplier. It also defines the specific conditions to be satisfied for conditional information requirements to become mandatory. The information requirements listed in the IRS provide references to the source of the requirement.
The IOGP S-732 specification documents follow a common structure (as shown below) comprising a specification, also known as a technical requirements specification (TRS), a procurement data sheet (PDS), this IRS and a quality requirements specification (QRS). These four specification documents, together with the purchase order, define the overall technical specification for procurement.
JIP33 Specification for Procurement Documents Information Requirements Specification (IRS)
This IRS is to be applied in conjunction with the specification, the PDS and the QRS, referred to in this document as IOGP S-732, IOGP S-732D and IOGP S-732Q respectively. Further information on the purpose of these documents and the order of precedence for their use is provided in the introduction of the specification.
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Instructions
IOGP S-732L (1.1) Information Requirements for Low Voltage Motor Control Centers (UL)
Instructions
In response to invitation to tender (ITT)
Suppliers shall submit information as defined in column E 'Submit At Proposal' in 'Requirements' sheet and in accordance with the ITT instructions.
On award of purchase order (PO)
Specified information requirements shall be submitted in accordance with the purchase order information submission instructions. Suppliers shall prepare and submit the supplier master information schedule (SMIS) incorporating information requirements in accordance with column F 'First Issue Post Purchase Order' in the 'Requirements' sheet. The supplier shall demonstrate compliance with each IRS requirement either: a) by providing document number cross reference to the requirement in the SMIS; or b) if specified in the purchase order, by using column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet.
On completion of scope
Suppliers shall validate that the information delivered meets the IRS requirements either: a) through cross reference to the deliverable type in a as-built version of the SMIS; or b) if specified in the purchase order, by providing an as-built version of the IRS with column J 'Fulfilled by Document Number(s)' in the 'Requirements' sheet populated with the specific document numbers issued to the purchaser.
IRS structure contents
| 1 | 'Front & preliminaries' sheet
The 'Front & Preliminaries' sheet comprises the standard JIP33 introductory sections: IRS front sheet, revision history table, acknowledgements, disclaimer, copyright notice, foreword and introduction.
| 2 | 'Instructions' sheet
The 'Instructions' sheet provides instructions that suppliers shall follow in response to this IRS.
| 3 | 'Requirements' sheet
The 'Requirements' sheet lists information requested during tendering and shall be supplied following award of the PO.
The information requirements are grouped under three broad categories:
— Contract Management Information Requirements Key information requirements relating to planning, managing, assuring and reporting the execution of the technical scope.
— Technical Information Requirements Technical information developed by the supplier or their sub-suppliers, during the execution of the PO.
— Purchase Order Specific Information Requirements Information requirements specified by the purchaser in addition to those detailed by the IRS to meet specific operational, project or legislative requirements.
The 'Requirements' sheet comprises columns A to L.
Column A — 'Code' contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Condition Invoking Requirement' identifies any specific conditions under which the information requirement is deemed to be needed.
Column D — 'Typical Deliverable' is provided for the purchaser to identify the deliverable type that the information would typically appear within. This also allows the purchaser's requisitioning engineers to group the various information requirements by deliverable type. This column accommodates names from CFIHOS document types.
Column E — 'Submit At Proposal' (Yes/No) defines if the information requirement is requested to be submitted with the supplier's proposal. Preliminary information submitted at proposal shall be matured and delivered to the purchaser as per the PO and delivery times identified in column G 'Weeks' and column H 'Period'. As default, column ‘Submit At Proposal’ is prepopulated for CAS D procurement.
Column F — First Issue Post Purchase Order, 'Purpose' (For Information / For Acceptance) is prepopulated for CAS D procurement. 'For Information' means that information is issued for information only. 'For Acceptance' means that the information is issued for client, or delegated authorised person/organisation, to review and accept the content for use in further equipment development activities. Information acceptance does not relieve the supplier of any PO responsibility or liability.
Column G and Column H — First Issue Post Purchase Order, ('Weeks' and 'Period') include durations for the first issue of the deliverable with respect to specific activities.
|  |  |  | (Period) | Long description
|  |  |  | WAD | Weeks After Delivery
|  |  |  | WAI | Weeks After Inspection
|  |  |  | WAO | Weeks After Order
|  |  |  | WAO (Monthly) | Weeks After Order Monthly
|  |  |  | WAT | Weeks After Test
|  |  |  | WPTD | Weeks Prior To Delivery
|  |  |  | WPTF | Weeks Prior to Fabrication
|  |  |  | WPTT | Weeks Prior To Test
Table 1 — Information submission abbreviations
Column I — 'Required As Built' (Yes/No), where "Yes" chosen, identifies any information requirements that shall incorporate all changes that have been made to the procured equipment original information prior to the completion of the PO.
Column J — 'Fulfilled by Document Number(s)' shall be used by the supplier to demonstrate compliance with the information requirement either: a) by providing document number cross reference to the information requirement in the SMIS; or b) if specified in the PO, by using this column within IRS.
Column K — 'Translation Required' (Yes/No) Specifies if the information requirement shall be translated into another language additional to the main language specified in the PO. 'Yes' means the information requirement should be translated into other language(s) additional to the main language (to be advised in contractual documentation). 'No' means to be provided in main language only.
Column L — 'Remarks' may include additional information needed to clarify the information requirement.
| 4 | 'Definitions' sheet
The 'Definitions' sheet comprises columns A to F.
Column A — 'Code' contains the JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
Column B — 'Information Requirements' contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
Column C — 'Description' provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
Column D — 'Reference' gives a reference to the IOGP JIP33 specification where the information requirement is identified.
Column E — 'Format' identifies the format of the relevant information deliverable to be submitted by the supplier as described in Table 2 below. Note: Project or software specific formats shall be specified by the purchaser by means of their hand over specifications.​
| Drop-down value​ |  | Definition​ |  |  | CFIHOS ID​
| Native​ |  | A native file is the default file format that a software application is designed to work with.​ |  |  | CFIHOS-60000835​
| PDF​ |  | A universal file format developed by Adobe® and standardized as ISO 32000 which preserves all the fonts, formatting, graphics, and colour of any source document, regardless of the application and platform used to create it. PDF’s must be in Optical Character Recognition (OCR) format which is text searchable and indexed. ​ |  |  | CFIHOS-60000933​
| Hardcopy​ |  | A permanent reproduction or copy of data which cannot be easily edited or manipulated, in the form of a physical object, of any media suitable for direct use by a person (e.g. paper).​ |  |  | CFIHOS-10000123​
Table 2 — Deliverable formats
Column F — 'CFIHOS Document Type Code' relates to the CFIHOS document type that is used to classify the document having this IRS content.
| 5 | Abbreviations and definitions
The following abbreviations, terms and definitions have been used in the various sheets of this workbook.
| buyer |  | organisation placing a contract or purchase order with supplier for equipment or services on project; may be alternatively referred to as 'user' or 'purchaser'
| CFIHOS |  | Capital Facilities Information Hand Over Specification
| company |  | project operating entity or the organisation the contractor is under contract to
| contractor |  | project contractor responsible for procuring equipment
| information |  | data, documents and/or models
| IRS |  | information requirements specification
| PDS |  | procurement data sheet
| PO |  | purchase order
| QRS |  | quality requirements specification
| SMIS |  | supplier master Information schedule
| supplier |  | organisation supplying equipment or services to the company and/or contractor on project; may alternatively be referred to as "vendor", "seller" or "manufacturer"
| TRS |  | technical requirements specification
| 6 | CFIHOS
The information requirements in the IRS are classified according to the IOGP JIP36 Capital Facilities Information Hand Over Specification (CFIHOS). The objective of mapping JIP33 IRS information requirements to CFIHOS is to facilitate value delivery across the supply chain through increased digitalization. ​Further information on CFIHOS can be found at:
https://www.jip36-cfihos.org
| 7 | Document metadata
Typical metadata for Information deliverables to be provided by suppliers in the SMIS is shown in Table 3. Metadata listed below is as per CFIHOS defined document properties (metadata) defined in CFIHOS C-SP-001 CFIHOS Specification Document, chapter Document properties (metadata).
| Name |  |  | Definition |  |  | CFIHOS unique ID
| Document number |  |  | The unique identifier for the 'document' according to the 'owner/operator' document numbering scheme. |  |  | CFIHOS-10000154
| Document revision code |  |  | A code used to identify the content of a document at a certain point in time. |  |  | CFIHOS-10000162
| Document title |  |  | A description, in a short and concise manner, of the content of the document. |  |  | CFIHOS-10000168
| Document revision date |  |  | The date the document was revised. |  |  | CFIHOS-10000076
| Originator company |  |  | The name of the company who has generated the document revision. |  |  | CFIHOS-10000077
| Document revision author |  |  | The name of the person who created the document revision. |  |  | CFIHOS-10000078
| Document revision approver |  |  | The name (or the User ID) of the person who has approved the document revision. |  |  | CFIHOS-10000079
| Document revision file name |  |  | The name of the electronic file (including the file extension) with the full path. When this attribute is populated the attribute physical storage location shall be left empty. |  |  | CFIHOS-10000080
| Originator document number |  |  | The unique identifier for the Document according to the originator document numbering scheme. |  |  | CFIHOS-10000160
| Originator document revision code |  |  | A code used to identify the content of a document at a certain point in time according to the originator which doesn't necessarily conform to the Owner/Operator's document revision coding scheme. |  |  | CFIHOS-10000081
| Document status code |  |  | The status of the document revision. |  |  | CFIHOS-10000083
| ISO language code |  |  | The primary language that the document revision is written in. |  |  | CFIHOS-10000147
| Document type short code |  |  | A code that uniquely identifies a document type. |  |  | CFIHOS-10000100
| Project code |  |  | The code that identifies the project the document revision refers to. |  |  | CFIHOS-10000161
| Document revision comment |  |  | Any additional comment / explanation for a document revision. |  |  | CFIHOS-10000085
| Plant code |  |  | The plant that the document revision is related to. |  |  | CFIHOS-10000005
| Export control classification code |  |  | A code that uniquely identifies an export control classification. |  |  | CFIHOS-10000086
| Transmittal number |  |  | The transmittal through which this document revision was communicated. |  |  | CFIHOS-10000087
Table 3 — Supplier deliverable metadata
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Requirements
IOGP S-732L (1.1) Information Requirements for Low Voltage Motor Control Centers (UL)
Requirements
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Condition Invoking Requirement — Describes condition(s) under which the information requirement is required (e.g. service offshore and weight greater than one tonne means information is required). Note: if blank, always required.
D | Typical Deliverable — Purchaser to advise the short description of the information deliverable that would typically include this information requirement.
E | Submit At Proposal — 'Yes' or 'No', where ‘Yes' means the information requirement is required to be submitted with the supplier's proposal or 'No' is not required.
F, G & H | First Issue Post Purchase Order — Issue purpose ('For Information' or 'For Acceptance'), time in weeks for issue of the information requirement and period defined after the purchase order placement. See the 'Instructions' sheet, Table 1 for full description of codes use in column H 'Period'.
I | Required As Built — Any information incorporating all changes that have been made to the procured equipment original information prior to the completion of the purchase order.
J | Fulfilled by Document Number(s) — Identifies which information requirement(s) listed in the supplier master information schedule (SMIS) addresses the purchaser's requirements. Note: It should be noted that one information deliverable can fulfil more than one information requirement.
K | Translation Required — 'Yes' or 'No', specifies if the information requirement shall be translated into another language additional to the main language specified in the purchase order.
L | Remarks — Additional information needed to clarify the information requirement.
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Requirement | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s) | Translation Required | Remarks
|  |  |  | (Yes/No) | Purpose | (Weeks) | (Period) | (Yes/No)
Contract Management Information Deliverables
S732v2-IR-1 | Supplier master information schedule |  | Information deliverables list | No | For Acceptance |  | WAO | Yes |  | No
S732v2-IR-2 | Delivery schedule |  | Delivery/production schedule | Yes | For Information |  | WAO | No |  | No
S732v2-IR-3 | Progress report |  | Progress report | No | For Information |  | WAO (Monthly) | No |  | No | Standard deliverable.
S732v2-IR-4 | Quality plan | Required for CAS A and B | Quality plan | - | - |  | - | - |  | -
S732v2-IR-5 | Sub-vendor delivery schedule | Required for CAS A and B | Sub-supplier list | - | - |  | - | - |  | -
S732v2-IR-6 | Inspection and test plan (ITP) for complete package |  | Inspection and test plan (ITP) | No | For Information |  | WAO | No |  | No
S732v2-IR-7 | Handling, lifting, shipping, storage and preservation procedure |  | Handling, shipping and storage procedure | No | For Information |  | WPTD | No |  | No
S732v2-IR-8 | Non-conformance records |  | Nonconformance history | No | For Acceptance |  | WAO | Yes |  | No
S732v2-IR-9 | Concession requests |  | Concession request | Yes | For Acceptance |  | WAO | Yes |  | No
S732v2-IR-55 | Pre-production planning (minutes of meeting) | Required for CAS A, B and C | Minutes of meeting | - | - |  | - | - |  | - | Standard deliverable.
Technical Information Deliverables
S732v2-IR-20 | Wiring diagram |  | Wiring diagram | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-22 | Single line diagram |  | Single line diagram | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-23 | Schematic diagram |  | Schematic diagram | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-24 | Name plate drawing |  | Name plate drawing | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-25 | General arrangement diagram |  | General arrangement diagram | Yes | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-27 | Detailed drawing |  | Detailed drawing | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-52 | Equipment specification sheet |  | Equipment specification | No | For Acceptance |  | WAO | Yes |  | No | Part of the drawing submittal package.
S732v2-IR-28 | Communication block diagram |  | Block diagram | Yes | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings. Part of the drawing submittal package.
S732v2-IR-30 | Cable size calculation | Required for CAS A and B | Cable size calculation | - | - |  | - | - |  | -
S732v2-IR-31 | Heat dissipation calculation and loads |  | Heat dissipation calculation and loads | No | For Information |  | WAO | No |  | No
S732v2-IR-32 | Reliability and availability calculations, and obsolescence plan | Required for CAS A, B and C | Reliability, availability, safety integrity level calculation | - | - |  | - | - |  | -
S732v2-IR-33 | Certificate of conformance |  | Certificate of conformance | Yes | For Information |  | WAO | Yes |  | No | UL 845 listing and arc resistance certifications
S732v2-IR-51 | Type test certificate of conformance | Required for CAS A and B | Certificate of conformance | - | - |  | - | - |  | -
S732v2-IR-34 | Regulatory compliance certificate |  | Regulatory compliance certificate | No | For Information |  | WAO | Yes |  | No
S732v2-IR-35 | Application software |  | Application software | No | For Information |  | WAO | Yes |  | No | Only when required by the data sheet.
S732v2-IR-36 | Bill of materials |  | Bill of materials | No | For Acceptance |  | WAO | Yes |  | No | Native format for drawings is only required for the as built stage not for approval drawings.
S732v2-IR-39 | Spare part list |  | Spare part list | No | For Information |  | WAO | Yes |  | No
S732v2-IR-41 | Commissioning instruction |  | Commissioning instruction | No | For Information |  | WAO | Yes |  | No
S732v2-IR-42 | Installation manual |  | Installation manual | No | For Information |  | WAO | No |  | No | Installation manual index, if required, should be provided in first revision of the document. When index agreed, installation manual content shall be provided in subsequent revision of the document.
S732v2-IR-43 | Maintenance manual |  | Maintenance manual | No | For Information |  | WAO | No |  | No | Maintenance manual index, if required, should be provided in first revision of the document. When index agreed, maintenance manual content shall be provided in subsequent revision of the document.
S732v2-IR-44 | Operating manual |  | Operating manual | No | For Information |  | WAO | No |  | No | Operating manual index, if required, should be provided in first revision of the document. When index agreed, operating manual content shall be provided in subsequent revision of the document.
S732v2-IR-47 | Factory acceptance test (FAT) procedure |  | Factory acceptance test (FAT) procedure | No | For Acceptance |  | WPTT | No |  | No
S732v2-IR-49 | Routine test procedure |  | Routine test procedure | No | For Information |  | WPTT | Yes |  | No
S732v2-IR-50 | Factory acceptance test (FAT) records |  | Factory acceptance test (FAT) records | No | For Information |  | WAT | No |  | No
S732v2-IR-54 | Packing list |  | Packing list | No | For Information |  | WPTD | No |  | No
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Definitions
IOGP S-732L (1.1) Information Requirements for Low Voltage Motor Control Centers (UL)
Definitions
Column | Heading — Details and requirements
A | Code — Contains IOGP JIP33 unique record identification code specific to the individual information requirement for the particular equipment.
B | Requirement — Contains data, documents or models to be provided by suppliers, based on the industry standard or IOGP JIP33 specification.
C | Description — Provides a description of the information requirement based on an industry standard, or developed by IOGP JIP33 or JIP36 (CFIHOS).
D | Reference — Reference to the IOGP JIP33 specification where the information requirement is identified.
E | Format — Defines the required format of the relevant information requirement to be submitted by the supplier.
F | CFIHOS Document Type Code — CFIHOS document type code that is used to classify the document having this IRS content.
Col A | Col B | Col C | Col D | Col E | Col F
Code | Requirement | Description | Reference | Format | CFIHOS Document Type Code
Contract Management Information Deliverables
S732v2-IR-1 | Supplier master information schedule | Schedule of specific information deliverables developed by the supplier and accepted by the purchaser to meet the information requirements defined in the agreed information requirements specification (IRS). The schedule typically defines: a. information deliverable type, title/description; b. unique identification (code/number) in the supplier's format unless agreed otherwise in the contract; c. planned submission arrangements including purpose, formats, timing, frequency. Arrangements for managing submissions, tracking progress and updating the schedule during the execution of the contract scope will be in accordance with contractual agreements. | Annex H | Native | CFIHOS-70000099
S732v2-IR-2 | Delivery schedule | Schedule depicting, as applicable to the service or product scope, design, supply, manufacture, inspection, testing and delivery activities to be executed by supplier/sub-supplier. Schedule details typically include: a. contractual milestones; b. activity early/late start/completion dates, durations, dependencies (calendar dates); c. critical path and float; d. outsourced services and equipment (cross referenced to purchase order and supplier); e. information deliverable submission dates identifying any execution activity dependencies. Progress against planned dates is measured and the schedule updated and reported to the [purchaser] in accordance with contract reporting agreements. NOTE: Schedule development tools, formats and submission protocols follow the supplier's standard practice unless otherwise agreed in the contract. |  | PDF | CFIHOS-70000298
S732v2-IR-3 | Progress report | Report detailing the activities completed in the period, percent complete against planned, activities planned for the next period, risks/areas of concern, cause of any delays and proposed recovery plans, concessions, internal and outsourced inspection and audit activities. NOTE: The frequency and scope of the progress report may also be modified by the terms and conditions in the purchase order. |  | PDF | CFIHOS-70000300
S732v2-IR-4 | Quality plan | Plan specifying the actions, responsibilities and associated resources to be applied by the [vendor], and when applicable [sub-vendors] or [manufacturers], to deliver the services or procured item(s) in conformance with the agreed requirements. ISO 9001:2015, 8.1 and ISO 10005 may be used to inform the development of quality plans for specific applications, processes or products. API Spec Q2 may be used to inform the development of service quality plans. |  | PDF | CFIHOS-70000451
S732v2-IR-5 | Sub-vendor delivery schedule | Definition of processes, products or services that will be externally provided and the controls to be applied by the supplier to ensure conformance with agreed requirements. The schedule includes evidence of the basis of capability assessment , quality management system certification (or equivalent), process or product qualification for proposed suppliers of outsourced products and services when nominated in the contract or quality requirements specification (QRS) . NOTE: ISO 9001, API Spec Q1 and API Spec Q2 define requirements for assessing risks and establishing controls for outsourced products and services. |  | Native | CFIHOS-70000455
S732v2-IR-6 | Inspection and test plan (ITP) for complete package | Tabular presentation of a quality plan typically used for process or product applications to define the specific sequence of operational activities, instructions, acceptance criteria records and associated supplier, purchaser and independent party conformity assessment activities. ISO 9001:2015, 8.1 and ISO 10005 may be used to inform the development of inspection and test plans for specific processes and products. | 9.22.1, 9.22.2, H.6.2 | PDF | CFIHOS-70000180
S732v2-IR-7 | Handling, lifting, shipping, storage and preservation procedure | Definition of practices to be followed during the storage, transport, lifting and preservation of the equipment and materials included in the scope of supply to maintain their functionality and guarantees. Procedures typically define: a. packaging requirements including contents, identification, size, weight and number of packages/container(s); b. special packing/unpacking/handling and lifting requirements; c. storage location and requirements; d. preservation requirements detailing inspection periods and required maintenance, materials required etc., both prior to installation and post installation, but prior to commissioning; e. drawings indicating the size of shipping splits, center of gravity, weight, identification, and packing list of contents. NOTE: Copies of applicable lifting procedures are included in the delivery documentation which accompanies shipments of equipment. | 8.1.2.6, H.4.3, H.5.2, H.5.3, H.5.4 | PDF | CFIHOS-70000154
S732v2-IR-8 | Non-conformance records | Details of non-conformances raised by or to the supplier/sub-suppliers against technical requirements during manufacturing prior to or during the delivery of the products or services. Non-conformance is managed by the supplier in accordance with ISO 9001:2015, 8.7 and associated records typically include description of non-conformance, analysis and disposition, correction implemented and details of any retesting or inspection taken to demonstrate subsequent conformance. NOTE: Instances where the proposed disposition is to accept a non-conforming condition are subject to agreement by the purchaser in accordance with the concession management protocols defined in the contract. |  | PDF | CFIHOS-70000226
S732v2-IR-9 | Concession requests | Formal submission seeking [purchaser] agreement to accept deviations from the contracted scope or technical requirements. Requests may be raised as a result of, as examples, material or service availability, obsolescence, innovation, non-conformance. Requests are typically raised as required during execution with a summary report detailing concessions raised, [purchaser] directions, agreed action status provided with progress reports and at contract closeout |  | PDF | CFIHOS-70000260
S732v2-IR-55 | Pre-production planning (minutes of meeting) | Minutes of meeting from a pre-production planning. Items to be covered during this meeting includes ITP, point of contact for supplier and third-party inspection company, overall quality process and inspection schedule. |  | PDF | CFIHOS-70000223
Technical Information Deliverables
S732v2-IR-20 | Wiring diagram | Diagram providing information on the circuitry of an object. Mandatory content of information: a. graphical symbols representing the objects; b. graphical symbols representing the connections among objects; c. reference designations; d. terminal designations; e. signal level conventions (applicable to logic signals); f. information necessary to trace paths and circuits (signal designations, location references); g. supplementary information necessary for the understanding of functions; h. point to point wiring details. Optional content of information: a. technical data; b. reference to other documents; c. information about wiring performance; d. cable and cable core identification. | 5.1.3, 5.2.1, 5.2.2, 6.2.1, 6.2.2, 6.3.74, 6.3.75, 8.2.11, 8.2.13, 8.2.19, 8.2.20, 8.2.32.1, 8.2.36.3, 8.2.40, 8.2.43.1, 8.2.43.3 | Native | CFIHOS-70000268
S732v2-IR-22 | Single line diagram | A diagram depicting the major equipment items (motors, switchboards, transformers etc.) and their relationships within the facility electrical distribution system including details of fault levels, current ratings, fixed or withdrawable equipment unit type, and voltage ratings. | 5.1.3, 5.1.4, 5.3.2.2, 5.3.3, 5.4.1.5, 5.4.4.3, 6.2.1, 6.2.2, 6.4, 8.2.11, 8.2.12.1, 8.2.19, 8.2.20, 8.2.35, 8.2.36, 8.2.37, 8.2.38, 8.2.39 | Native | CFIHOS-70000371
S732v2-IR-23 | Schematic diagram | A pictorial representation of the main elements and functions of a control circuit for electrical equipment with input/output sources (switches, relays, etc.) and their relationships, details logic functions of the circuit and individual schematics for each unit type and designation. | 5.1.3, 5.2.1, 5.2.2, 8.2.11, 8.2.13, 8.2.19, 8.2.20, 8.2.35, 8.2.36, 8.2.37 | Native | CFIHOS-70000328
S732v2-IR-24 | Name plate drawing | A drawing that depicts the layout, font size, and lettering information for the identification of equipment tag names that will be illustrated on the nameplates that will be installed on the individual equipment items. This includes the material of the nameplate and fastening method. | 5.1.3, 6.1, 6.2.2, 6.3.64, 6.3.73, 6.3.75, 8.2.38, 8.2.39 | Native | CFIHOS-70000445
S732v2-IR-25 | General arrangement diagram | A drawing showing overall dimensions, critical interface dimensions, part references and weight of assemblies, equipment and components. The drawing shall contain reference to main specifications and standards. For equipment/components, the drawing may include cross sectional views. The document may contain the following information: a. main dimensions; b. interface connections; c. weight; d. center of gravity; e. withdrawal/installation and maintenance space; f. installation and mounting details; g. lifting arrangement; h. shipping split details; i. elevation views. | 5.1.3, 6.1, 6.3.74, 6.3.75, 8.1.2.6, 8.2.11, 8.2.12,8.2.19, 8.2.20, 8.2.34, 8.2.35, 8.2.36.3, 8.2.37, 8.2.38, 8.2.39, 8.2.4.6, 8.2.40, 8.2.42, 8.2.43.2, 8.2.6.2, 8.2.6.3, 8.2.9 | Native | CFIHOS-70000153
S732v2-IR-27 | Detailed drawing | Drawing or detail illustrating parts of a construction or a component, generally enlarged, including specific information about the form and construction or about the assembly and joints. Also supports other documents where a cross-sectional view, side view or part list is necessary for clarity. A view or drawing that shows what the inside of equipment looks like after a cross-sectional cut has been made. These details may be part of another drawing or included in a document. The details necessary include: bus bar splices or connections, bus bar torqueing requirements, cable termination hole patterns, cable gland plate locations, floor mounting details including hold down bolt locations and sizes, side views of bus duct and cable bus connections, views for ventilation covers or filter locations, arc resistance construction installation details (space above, safe clearance zones, cable entry, plenum requirements), other details for regulatory compliance certificates (tilt and roll requirements, drip shield, hand rails, guard rails, seismic installation details). | 5.1.3, 8.2.10.6, 8.2.11.28, 8.2.13.21, 8.2.16, 8.2.29, 8.2.34, 8.2.9 | Native | CFIHOS-70000438
S732v2-IR-52 | Equipment specification sheet | A specification or drawing that describes the physical equipment and technical details for the purpose of procurement or fabrication. It complements the data sheet. This includes, but is not limited to, details such as: a. all busing details including ratings, plating, and insulation requirements; b. space heater requirements; c. incoming and outgoing cable requirements; d. shipping split arrangements; e. voltage and current ratings including ambient conditions; f. specific application requirements (arc resistance construction features, marine/offshore, regulatory, etc.); g. incomer type and details; h. metering, protective relaying, and overload type details; i. communication, networking, and CBM requirements; k. dimensional data needed to perform arc flash incident energy calculations (IEEE 1584): 1. between each phase of the horizontal bus; 2. between each phase of the vertical bus; 3. between each phase of conductors terminating on the line side of the unit overcurrent protection devices (for each rating provided); 4. size of the unit (this can be the smallest unit provided). | 6.3.46 , 5.1.4, 5.3.2.1, 6.2.1, 6.2.2, 6.2.3, 6.4, 8.1.2, 8.1.7.2, 8.1.9, 8.2.10, 8.2.11, 8.2.12, 8.2.13, 8.2.2.10, 8.2.34, 8.2.35, 8.2.36, 8.2.37, 8.2.38, 8.2.39, 8.2.4, 8.2.40, 8.2.42, 8.2.43, 8.2.6, 8.2.8.2, 8.2.9, H.5.1 | PDF | CFIHOS-70000399
S732v2-IR-28 | Communication block diagram | The block diagram depicts the interconnected networks, cables and connections. Mandatory content of information includes: a. direction of main interfaces between communication equipment items; b. denomination of incoming and outgoing communication circuits; c. communication protocol designations and details (e.g. routers, hubs, ports, switches). | 5.1.3, 8.2.41.1, 8.2.43.1 | Native | CFIHOS-70000237
S732v2-IR-30 | Cable size calculation | Calculations required for sizing of power cables internal to the MCC (e.g. cable connections from incoming breaker to main bus, internal transformer feed, transition section, etc.). This is required if a temperature rise test for the specific application is not available. | 8.2.35 | Native | CFIHOS-70000034
S732v2-IR-31 | Heat dissipation calculation and loads | This document contains the calculation by the supplier to arrive at the heat load produced by the MCC to enable HVAC sizing and includes load factors and type of load provided to the supplier to produce accurate calculation. | 8.2.37, 8.2.38, 8.2.39 | PDF | CFIHOS-70000441
S732v2-IR-32 | Reliability and availability calculations, and obsolescence plan | Demonstrates starting and operating reliability/availability of purchased equipment (e.g. mean time between failure data) calculations. This also provides details of the equipment obsolescence plan. | 4.3.1, 4.3.3, 4.4.2, 4.4.3 | PDF | CFIHOS-70000312
S732v2-IR-33 | Certificate of conformance | A statement of conformity where attestation is performed by the person or body that is independent of the person or organization that provides the object, and of user interests in that object (third party). This includes the UL 845 certification (listing mark). | 5.1.5, 6.2.3, 7.3, 8.1.2, 8.2.10.5, 8.2.4.8 | PDF | CFIHOS-70000013
S732v2-IR-51 | Type test certificate of conformance | The results of test performed to provide evidence that the design meets the arc resistance construction requirements of IEEE C37.20.7, including the methodology used to achieve the arc resistant rating. When specified, type test shall be independently verified by a third party and supported by a certificate of conformance. This may also be included in the UL 845 certificate of conformance. NOTE: UL witnessing of the supplier's arc resistance tests does not satisfy this requirement. | 5.1.4, 6.2.3, 8.1.2, 8.2.4.8 | PDF | CFIHOS-70000013
S732v2-IR-34 | Regulatory compliance certificate | A document certifying conformity to local regulations which accompanies shipment of equipment and/or goods. e.g. official certificate issued by OEM/supplier or approved licensed agent of OEM/supplier. This includes USCG, ABS or DNV type certifications or similar designations. | 7.3, 8.2.19, 8.2.20 | PDF | CFIHOS-70000079
S732v2-IR-35 | Application software | A computer program designed for a specific task or use including configuration, monitoring, diagnostics, and operations of control, protective, and communication devices within the MCC. Examples include ASDs, soft starters, trip units, condition-based monitoring, metering devices and microprocessor overload relays. | 8.2.37, 8.2.43.1, 8.2.43.2 | Native | CFIHOS-70000012
S732v2-IR-36 | Bill of materials | A list of parts, components and sub-assemblies for equipment with part numbers, item numbers, quantities, material designations and references to specifications. NOTE: When agreed, it includes details of sub-suppliers. | 6.3.74, 6.3.75, 6.4, 8.2.10.5, 8.2.11, 8.2.16.1, 8.2.19, 8.2.2.10, 8.2.20, 8.2.35, 8.2.36, 8.2.37, 8.2.38, 8.2.39, 8.2.4.8, 8.2.40, 8.2.41.1, 8.2.42, 8.2.43, 8.2.6.2, 8.2.6.3, 8.2.9 | Native | CFIHOS-70000028
S732v2-IR-39 | Spare part list | Table containing list items specifying the objects (parts, components, software, equipment, etc.) that are available or delivered as spare parts for later use. Mandatory content of information: a. item reference number (BOM); b. quantity; c. part number; d. part name. | 8.2.11, 8.2.35, 8.2.36, 8.2.37, 8.2.38, 8.2.39, 8.2.40, 8.2.42, 8.2.43.1 | PDF | CFIHOS-70000374
S732v2-IR-41 | Commissioning instruction | Instruction providing information on the commissioning of the product. Instructions for commissioning are provided especially for large and highly complex products and for large industrial installations. The purpose of such instructions is to provide the user with the information needed for initial setting-up of the product. Mandatory content of information: These instructions contain for example: a. download program, software instructions ; b. checks to be performed before connection to the supply network and before first operation; NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard installation, operation and maintenance manual or as a standalone document. | 8.2.10.5, 8.2.11.18, 8.2.19, 8.2.20, 8.2.37, 8.2.9 | PDF | CFIHOS-70000396
S732v2-IR-42 | Installation manual | Description of methods of installing a piece of equipment. Installation refers to the mounting, setting, erection, etc. NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard installation, operation and maintenance manual or as a standalone document. | 8.1.2, 8.1.7.2, 8.1.9, 8.2.10, 8.2.11.29, 8.2.12.9, 8.2.16, 8.2.19, 8.2.20, 8.2.29, 8.2.34.1.4, 8.2.4.6, 8.2.9, H.4.3, H.5.1, H.6.1 | PDF | CFIHOS-70000181
S732v2-IR-43 | Maintenance manual | Description of methods of maintaining a specific piece of equipment. Typically originates from the equipment or package supplier. NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard installation, operation and maintenance manual or as a standalone document. | 8.1.2.8.7, 8.1.7.2, 8.1.9, 8.2.10, 8.2.11, 8.2.12.9, 8.2.16, 8.2.2.10, 8.2.35, 8.2.36, 8.2.37, 8.2.38, 8.2.39, 8.2.4.6, 8.2.40, 8.2.42, 8.2.43, 8.2.9, H.4.3, H.5.1 | PDF | CFIHOS-70000206
S732v2-IR-44 | Operating manual | Description of methods of operating a piece of equipment or process unit, including instructions, procedures, drawings, tables, etc. for the operation: energization, switching and isolation. Including operational limits, function testing, possible interruptions, corrective actions, hazards and corrective measures to be taken. This normally includes the cut sheets and technical specification details for the components supplied as part of the MCC assembly. This also includes time current curves (TCC) for the protective devices that can be utilized in the electrical protection coordination studies by others. NOTE: Unless otherwise agreed, can be delivered as part of supplier's standard installation, operation and maintenance manual or as a standalone document. | 8.2.10.4, 8.2.10.5, 8.2.11.18, 8.2.2.10, 8.2.36.3, 8.2.37, H.4.3, H.5.1 | PDF | CFIHOS-70000228
S732v2-IR-47 | Factory acceptance test (FAT) procedure | The FAT procedure will be used to ensure a common understanding of performed testing and acceptance criteria. This document shall include all testing activities and their acceptance criteria according to applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Test set-up and test equipment are to be defined. Suppliers' standard (routine) test procedures should be used as far as possible. This will include all the functional tests as specified in the technical specification. | 5.2.2, 8.2.11.17.6, 8.2.11.28, 8.2.36.3, 9.22.1, 9.22.2, H.6.2 | PDF | CFIHOS-70000427
S732v2-IR-49 | Routine test procedure | Procedure documenting the supplier's recommended testing activities and acceptance criteria in accordance with the applicable standards, specifications and requirements, to document the condition of the equipment as tested from factory. Procedure to define test set-up and test equipment. | 9.22.1, 9.22.2, F.2 | PDF | CFIHOS-70000332
S732v2-IR-50 | Factory acceptance test (FAT) records | The FAT report will be used to verify that the equipment has been tested according to FAT procedure. The FAT report will be used for acceptance of the equipment delivery This document shall include all testing activities and their acceptance criteria, in accordance with the FAT procedure, to applicable standards, specifications and requirements to document the condition of the equipment as tested from factory. Test set-up and test equipment shall be defined. All equipment that was disconnected to facilitate the AC withstand testing (see F.2) and reconnected afterwards shall be documented in the FAT report. | 6.3.46 , 5.2.2, 8.2.11.17.6, 8.2.11.28, 8.2.36.3, 8.2.41.1, 9.22.1, 9.22.2, F.2, H.6.2 | PDF | CFIHOS-70000429
S732v2-IR-54 | Packing list | A detailed list of the equipment packaged and shipped. | H.5.1, H.5.2, H.5.3, H.5.4 | PDF | CFIHOS-70000269
Purchase Order Specific Information Requirements
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft
Public Review Draft

## Back Cover
Public Review Draft

## Pick Lists (hidden)
Deliverables Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F | Col G | Col H | Col I | Col J | Col K | Col L
Code | Title | Condition Invoking Requirement | Typical Deliverable | Submit At Proposal | First Issue Post Purchase Order |  |  | Required As Built | Fulfilled by Document Number(s)� | Translation Required | Remarks
|  |  |  | Yes/No) | Purpose | (Weeks) | (Period) | Yes/No)
|  |  |  | Yes | For Information |  | WAD | Yes |  | Yes
|  |  |  | No | For Acceptance |  | WAI | No |  | No
|  |  |  | - | - |  | WAO | - |  | -
WAO (Monthly)
WAT
WPTD
WPTF
WPTT
-
Definitions Tab Pick Lists
Col A | Col B | Col C | Col D | Col E | Col F
Code | Title | Description | Reference | Format | CFIHOS Discipline Document Type Code
Hard Copy
Native
PDF
Intelligent Vector (CAD)
Multi media (Film)
Raster Image (Bitmap)
Structured Data (MS Apps)
Technical Publication (Text)
-
Note on K4: Chris Mitchell:
Note on L4: Chris Mitchell: